## ERCOT Operations Report

## ROS & OWG

## October 2003

October-Frequency control issues (High or Low Frequency) 59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | Max | SCE | (Largest QSE Change) |
| 10/2/2003 0:00 | 60.1090 | 24796 | -285 | 667 | -800 (-300) |
| 10/3/2003 22:02 | 59.8700 | 29749 | 319 | -1331 | -3000 (-900) |
| 10/5/2003 9:05 | 59.8990 | 26669 | 437 | -266 | 4250 (1150) |
| 10/6/2003 6:05 | 59.8970 | 28063 | 787 | -835 | 2000 (550) |
| 10/6/2003 16:30 | 59.8800 | 38542 | 710 | -1449 | n/a |
| 10/8/2003 5:43 | 60.1090 | 26904 | -243 | 874 | 1650 (400) |
| 10/8/2003 6:08 | 59.8900 | 28501 | -65 | -113 | 1650 (400) |
| 10/8/2003 22:04 | 59.8870 | 34763 | 168 | -950 | -2700 (-1100) |
| 10/8/2003 22:16 | 60.1020 | 34383 | 460 | 92 | -600 (-400) |
| 10/13/2003 22:03 | 59.8900 | 34205 | 312 | -1025 | -3600 (-950) |
| 10/14/2003 1:07 | 60.1130 | 26520 | -230 | 94 | -350 (-150) |
| 10/14/2003 6:34 | 60.1020 | 30178 | 391 | -176 | n/a |
| 10/15/2003 6:10 | 59.8890 | 25283 | -85 | -235 | 3800 (950) |
| 10/15/2003 6:48 | 60.1040 | 27396 | 121 | 314 | n/a |
| 10/17/2003 18:10 | 60.1090 | 34780 | -950 | -701 | n/a |
| 10/18/2003 0:03 | 59.8960 | 24827 | -237 | -523 | -1600 (-350) |
| 10/21/2003 0:06 | 60.1110 | 25103 | -534 | 26 | -1400 (-350) |
| 10/24/2003 0:07 | 60.1050 |  |  | data not |  |
| 10/24/2003 6:10 | 59.8850 |  |  | currently |  |
| 10/24/2003 22:10 | 59.8880 |  |  | available |  |
| 10/27/2003 17:58 | 59.8710 | 30090 | 710 | -1197 | n/a |
| 10/28/2003 6:07 | 59.8920 | 25738 | 18 | -310 | 3250 (750) |
| 10/29/2003 5:22 | 60.1090 | 22571 | -165 | 550 | n/a |

| Time | Frequency | Resource lost | ### Pre disturbance information |
| --- | --- | --- | --- |
| 10/6/2003 17:28 | 59.8700 | Resource trip: 550 MW | ### DC Tie. Frequency normal, ~450 MW down Reg. Load ~ 38000 but looks suspect. |
| 10/7/2003 13:33 | 59.8090 | Resource trip: 700 MW | -275 SCE Prior to trip |
| 10/11/2003 12:08 | 59.8990 | Resource trip: 850 MW |  |
| 10/31/2003 3:18 | 59.8770 | Resource trip: 500 MW |  |
| 10/31/2003 6:08 | 59.8870 | Resource trip: 100 MW | ### Across Large Sched change |
| 10/31/2003 11:24 | 59.7940 | Resource trip: 800 MW | ### Pre disturb F 59.975 |
| 10/31/2003 12:22 | 59.8470 | Resource trip: 450 MW | Pre disturb F 59.945 |

October-Locations and Relative Activity Capacity Purchases for OOMC & RMR

October-Locations and Relative Activity of Congestion Management

Occurrences for October of 2 days or less, listed below:

Allen -Renner & P Tenn			Nacogdoches – Herty N

Asherton – Eagle Pass				North - Houston

Athens Tap – Athens North			Polk – Hall Acres

Big Brown – Venus Sw				Rio Grand - La Grulla

Collin - Bridges					Pearsall – San Miguel

DFW Autos					Seagoville Sw Auto

Garrot – Thermal Energy 			Valley – Anna Sw

Gibbons Creek – Twin Oaks			Venus-Webb-Cedarhill

Graham-Parker-Benbrook			Watermill - Liggett

Laredo – Falfurrias				Watermill – West Levee

Las Milpas – S McAllen			West Levee – East Levee

Lydell - Cardiff					Whitepoint - STP

Magic Valley – Weslaco			Wind Farms

N Laredo – Mines Rd				Zorn-Lytton/Austrop

*Days of units purchased for some time in the area described.  Data taken from daily reports and is approximated for global overview purposes only.

New Procedures/ Forms/ Operations Bulletins

| 10/15/2003 | ERCOT Power Operations Bulletin 52 | Revised actions to be taken on Day Ahead desk if AS shortages detected |
| --- | --- | --- |
| 10/17/2003 | ERCOT Power Operations Bulletin 51 | Revision to Day Ahead Desk requiring notification of Shift Supervisor when a shortage of AS detected |
| 10/15/2003 | ERCOT Power Operations Bulletin 50 | Revision to the Frequency Control Desk updating valid QSE names |
| 10/15/2003 | ERCOT Power Operations Bulletin 49 | Revision to the Transmission & Security Desk updating valid QSE names |
| 10/15/2003 | ERCOT Power Operations Bulletin 48 | Revision to Operating Period Desk addressing hour ahead study timing. |
| 10/10/2003 | ERCOT Power Operations Bulletin 47 | Revision to Frequency Control Desk clarifying that when a participant notifies ERCOT of unscheduled generation the operator will fill out a VDI form, but give no instruction to QSE. |
| 10/10/2003 | ERCOT Power Operations Bulletin 46 | Revision to Transmission & Security Desk refining the wording of posting alerts |
| 10/09/2003 | ERCOT Power Operations Bulletin 45 | Revision of Operating Period Desk deleting instructions on how to view displays |
| 10/02/2003 | ERCOT Power Operations Bulletin 44 | Temporary solution to provide TOs with information on Planned Outages that require movement of generation |
| 10/02/2003 | ERCOT Power Operations Bulletin 43 | Revision to the Operating Procedures development to add definition of a preparer, etc. |
| 10/02/2003 | ERCOT Power Operations Bulletin 42 | Revision of Operating Period Desk Procedures to remove requirement that operator check SPD status etc. |
| 10/02/2003 | ERCOT Power Operations Bulletin 41 | Revision of Transmission & Security Desk to correct “reviewer” to “requestor” describing an outage requestor |
| 10/02/2003 | Operating Procedures Development & Maintenance V2R2 | Update to current practices after additional operator reviews. |
| 10/15/2003 | Frequency Control Desk V2R9 | Update to current practices after additional operator reviews. |
| 10/15/2003 | Operating Period Desk V2R8 | Update to current practices after additional operator reviews. |
| 10/15/2003 | Transmission & Security Desk V2R14 | Update to current practices after additional operator reviews. |
| 10/24/2003 | Day-Ahead Desk V2R11 | Update to current practices after additional operator reviews. |
| 10/29/2003 | Transmission Service Request Process | Update to current practices after additional operator reviews. |

# Security Alert Stage/ Threatcon/ Related issues

Security Threat Alert Yellow (Elevated) maintained through October.

OCN, Advisory, Alert, Emergency Notice and Major Events

| LOG DATE | START | END | LOG TYPE | COMMENTS |
| --- | --- | --- | --- | --- |
| 10/1 | 13:37 | 24:00 | Alert | Issued for N. Laredo – Mines Rd above 1st contingency limit. |
| 10/7 | 11:00 | 20:00 | Advisory | Issued for North to Houston. |
| 10/8 | 12:00 | 20:30 | Advisory | Issued for North to Houston. |

Significant Communication Problems

A lot of issues with the Portal after new Portal was brought up.

## Major Computer Systems Problems/ Fixes

None.

# Major system Voltage problems

None.

Blackout/Load Shed incidents

None.

ERCOT peak for last month (Unofficial)

10/13 17:00 39,106 (unofficial).

## Update on New Generation

Amoco Oil Unit approved for synchronization.

## Max Temperature

10/16 94.0 F in the Far West.

# New SPS & RAP’s

None.

# Other

Adjusted Laar per cent for Responsive Reserves from 35% to 50% during November.

Adjusted Frequency Bias setting to 533 MW/ .1 Hz.

PDCWG recommendation 533 October through April and 604 May through September based on average response over these periods.