## Sheet1
Testing Requirement | Protocol | Operating Guide | NERC Standards | Comments | Period of Assessment | Type of Assessment | Who is Assessed
Capacity and Energy Emergency Procedures |  | 4.5 | P5-T1 / P6-T1 | Identifies reasons and step requirements to initiate and recover from EECP. | On Going | Audit and investigations | QSE
AVR/PSS in service and in voltage control mode |  | Interim Reactive Std | IIIC-M4 | Describes Testing and Maintenance obligations | On Going | Audit/Investigation | PGC /QSE
24/7 Staffing and Communication Requirements | 4.3.4 | 3.1.4 |  | Explains that Generators greater than 10 mw shall be staffed and monitored 24 hours a day. | On Going | Audit/Investigation | PGC
12 Month Outage Scheduling | 8.1.3 |  | P4-T4 | Identifies the process of scheduling outages for Generation Resources in a 12 month rolling format. | Seasonal | Data Submittal | PGC
AVR Testing | 6.10.3.5 | 3.1.4.4 | II B S1-M4,M6 | The Generation Entity shall perform the unit automatic voltage regulator (AVR) tests and shall supply data as required by the NERC Planning Standards ...and the Operating Guides. | Once every 5 years if not requested sooner by ERCOT | Data Submittal | QSE & PGC
Biennial Reactive Testing | 6.10.3.5 | 3.1.4.3 | II B S1 M3 | Protocol 6.10.3.5 explains the requirements for Reactive testing. These tests are to be run at the ERCOT set date not more than every two years. Unit design capability numbers are to be included on the form found in ERCOT Guide 6.3.2 Test results and design capability should be close to the same. If they are not, there should be a limiting factor entered on the form to indicate why the unit can not perform to designed specifications. | Biennial | Data Submittal | QSE
Net Dependable Testing | 6.10.2 | 3.1.4.2 | II B S1-M2 | Protocol 6.10.2 explains that Unit Net Dependable testing must be scheduled prior to the season. There are exceptions if unit is less than 10 megawatts or will be run less that 168 hours for the season. Actual tests are to be run every season. Seasons are: Fall = September, October, November. Winter = December. January, February. Spring = March, April, May. Summer = June, July and August. | Seasonal | Data Submittal | QSE
Real Time Data | 6.5.1.1 | 8 | P4-T2 | Identifies the real time data requirements to be provided to ERCOT | On Going | Data Submittal | QSE
Supply of Generator models |  | 3.1.4 | IIA S1-M3 | Provides the minimum requirements for Modeling that ERCOT Requires | On Going | Data submittal | PGC
LAARS Testing | 6.10.2 |  |  | Describes Seasonal Test requirements of LAARs | On Going | Data Submittal | PGC
Black Start Service & Testing | 6.5.8 / 6.10.3.6 |  | IVA-M4 | Explains Black Start Services and Testing requirements for contract black start units | Annually | Data Submittal | PGC/QSE
Back Up Control Plan |  | 3.1.3.1 | P6-T3 (future) | Lists Requirements for a QSE backup control plan | Yearly | Data Submittal | QSE
Hydro Responsive Testing |  | 2.5.2.3 |  | Identifies requirements to be met by hydro supplying responsive reserve | On Going | Data submittal | QSE
Generation Under Frequency Relay Coordination |  | 3.1.4.6 | IIIC-M7 | Identifies Generator Under Frequency relay requirements in relationship to Distribution under frequency relay settings Generators should not trip off line prior to third step underfrequency relays operating in the Distribution system. | On Going | Data Submittal and Investigation | QSE
Compliance with Dispatch Instruction | 5.4.4 | 3.1.2 | P9 Section C / 3.4.3.3 | These sections relate to Valid Dispatch Instructions from the ERCOT Operator to QSEs. The Protocol and Guide language explains the requirements for Entities to adhere to these instructions and the process if a conflict occurs. Valid Instructions should be followed unless a personnel safety or equipment damage may result from that instruction. | On Going | Investigation | QSE
Voltage Support Performance | 6.1.7/ 6.5.7 | Interim Reactive / Voltage Standard | P2-B3 / IIIC-M2 | Identifies Generator Obligations in providing voltage support.AVR is service, staying within 2% of voltage profile, Supplying URL at TO request, accepting reactive requests from ERCOT above URL, and Taking acting upon requests of tap changes at the step up transformer | On Going | Investigation | QSE
Balancing Energy Performance Testing | 6.10.3.4 |  |  | Indicates testing requirements for Balancing Energy Performance | On Going | Performance Monitoring | QSE
Non-Spin Performance | 6.5.5 / 6.1..5.5 |  |  | Identifies requirements for units that produce non-spin ancillary services. | On Going | Performance Monitoring | QSE
OOMC Performance | 6.5.10(7,8) / 6.10.8 |  |  | Lists Responsibilities of QSE in supply of OOMC requested by ERCOT | On Going | Performance Monitoring | QSE
OOME Performance | 6.5.11 (5) / 6.10.7 |  |  | Lists Responsibilities of QSE in supply of OOME requested by ERCOT | On Going | Performance Monitoring | QSE
Regulation Performance | 6.10.5.3 |  |  | Identifies Regulation Performance criteria for QSEs. | On Going | Performance Monitoring | QSE
Responsive Reserve Performance | 6.10.3.2 |  |  | Indicates testing requirements for Responsive Reserve to be conducted by ERCOT | On Going | Performance Monitoring | PGC / QSE
Black Start Procedures |  | 4.6 | IVA.-M2 / IVA-M3 | This section provides general philosophies to be followed in the event of a partial or complete collapse of the ERCOT system. Timely implementation of a restoration plancompiled according to this guide should facilitatecoordination between ERCOT, QSEs, and Tos to ensure restoration of service to the ERCOT system at the earliest possible time. Those QSEs representing contracted Black Start Units will provide ERCOT with individual plant start-up procedures for coordination of their activities with those of the appropriate TO. | Annually | Plan Submittal | PGC / QSE