COMPLIANCE REPORT TO ROS

Dec. 8, 2003

- ERCOT Frequency Control Related Issues:

  - Continuing work with QSEs to review responses to letters of non-Compliance for Regulation measure – December scoring adjustment not complete at this time.

  - November’s ERCOT-wide CPS-1 monthly one-minute average frequency score increased to almost 139% from 125% in October (100 is minimum passing.)

  - Compliance looks forward to initial review of SCE performance during 0600 and 2200 periods.

  - TAC accepted ERCOT proposed changes to PRR436 and forwarded to the Board.  It was intended to ease Load participation in the market.  The provisions in the draft PRR to change balancing energy and responsive reserve performance criteria were made more limiting, applying more specifically to the LaaR part of a QSE portfolio.

- Transmission Security Issues:

  - There were no reported NERC Interconnect Reliability Limit (IRL) violations in November.  Operations and Compliance need to review the list of IRL candidates for 2004; probably these will not change from 2003.

  - ERCOT EMMS is developing a proposal to review transmission security for events below the NERC criteria.   Compliance will work with Operations and the EMMS development team to develop a project request.

- Resource Plan Performance Metrics –Compliance is focusing on reviews with individual QSE who have issues with these metrics to identify causes and cures, primarily to test validity of the measures when unique situations are present.  Drafting of a PRR to include these measures will begin in January.

- Generator real and reactive testing –   ERCOT Compliance will present rough numbers on amount of MVAR modeled in the system vs. tested at the Wednesday ROS meeting.   Compliance will work with Operations to identify need for retest of some units.

- NERC Issues –

  - NERC has finalized measures for assessment in 2004.  Of particular interest, those TDSPs with Undervoltage Load Shed in the Valley will need to provide an assessment of their systems to perform intended functions by the end of the year.

  - Cyber security standard draft enforcement will start in 2004 and only applies to ERCOT.   Drafting of a new standard underway; ERCOT is creating a group (ERCOT CIPAG) to review cyber and physical security issues.  Hopefully the ERCOT group will participate in the NERC standard development.

  - Operate Within Limits standard will be balloted in December and January 2004.  Transition from NERC Operating Policies to Standards has not been established, this may provide a test case.   The second posting of the Facilities Ratings standard is out for comments until January 29, 2004.  No others are up for ballot or review at this time.

- Protocol Compliance –Assessment details are in draft.  2004 enforcement includes posting of non-compliant entities.

- Investigations –

  - PRR461 on confidentiality passed PRS.  This would clarify that stakeholders working in ROS or its subgroups could view certain protected data to review abnormal events or performance before confidentiality timelines expire.  Status of generators is currently confidential for 6 months.  This got the needed ROS support.

  - Compliance is working with AEP and an unspecified QSE on review of August 7th event.  Investigation is focused on local effects.

  - Compliance gathered additional information confirming LaaR deployment and performance requested by ROS after the last meeting.  Several LaaR that did not operate where actually have awards at the time of the event; they were listed as unarmed in the resource plans.   More details at the ROS meeting.