## ERCOT Operations Report

## ROS & OWG

## November 2003

November-Frequency control issues (High or Low Frequency) 59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 11/3/2003 17:54 | 59.891 | 37759 | 790 | -97 | Underestimated lighting load over this interval |
| 11/3/2003 22:54 | 60.105 | 29475 | -662 | 921 | -1550 (-600) |
| 11/4/2003 18:10 | 59.866 | 38152 | -356 | -296 | 650 MW resource lost |
| 11/8/2003 10:25 | 59.879 | 28257 | -31 | -1237 | 650 MW resource lost |
| 11/4/2003 22:05 | 59.899 | 32195 | -241 | -267 | -3400 (-1250) |
| 11/8/2003 16:08 | 59.891 | 27128 | -93 | -128 | 275 MW resource lost. Pre - disturbance frequency 59.95 Hz. |
| 11/11/2003 6:07 | 59.893 | 25761 | -423 | -128 | Sudden 250 MW load increase during ramp |
| 11/11/2003 22:04 | 59.875 | 30418 | 251 | -1002 | -3200 (-1650) |
| 11/13/2003 0:05 | 60.116 | 24645 | -122 | 506 | -1350 (-550) |
| 11/15/2003 13:01 | 59.862 | 29607 | -148 | 63 | 575 MW resource lost |
| 11/15/2003 22:02 | 59.895 | 27827 | 413 | -561 | -1600 (-700) |
| 11/17/2003 20:05 | 59.849 | 32932 | -130 | 466 | 575 MW resource lost |
| 11/21/2003 17:45 | 59.896 | 31142 | 790 | -512 | No individual with low SCE; 450 MW of VDI's issued to recover frequency |
| 11/22/2003 11:15 | 59.860 | 29153 | -80 | 48 | 380 MW resource lost; pre disturbance frequency 59.96 |
| 11/23/2003 0:18 | 59.8 | 24990 | -21 | 274 | 580 MW resource lost |
| 11/23/2003 0:25 | 60.11 | 25040 | 249 | -31 | Over shoot during recovery |
| 11/24/2003 17:25 | 59.891 | 31206 | 70 | 105 | 360 MW resource lost; pre disturbance frequency 59.97 |
| 11/26/2003 5:53 | 59.81 | 25747 | -347 | 35 | 760 MW resource lost |
| 11/29/2003 4:03 | 59.827 | 26724 | -103 | 0 | 535 MW resource lost |
| 11/30/2003 16:31 | 59.836 | 25107 | 171 | 75 | 675 MW resource lost |

November -Locations and Relative Activity Capacity Purchases for OOMC & RMR

November-Locations and Relative Activity of Congestion Management

Occurrences for November of 2 days or less, listed below:

Abilene – SWRTP				MLSES-SCSES & ENTPR

Allen SW-Royse SW-MNSES			MNSES – Royse SW

Allen – P Tennyson				N McCallen – N Edin

Big Brown – Venus SW			North – Houston

Centerville Rd – Kirkland Park		O’brien Auto

E Mesquite – Mesquite Western		South – North

Forney – Elkton				South – Houston

Gibbons Crk – Twin Oaks			STP – Blessing

Lon Hill – Rio Hondo				Watermill – West Levee

MGSES – Odessa				Weslaco – N Weslaco

*Days of units purchased for some time in the area described.  Data taken from daily reports and is approximated for global overview purposes only.

New Procedures/ Forms/ Operations Bulletins

| Date | Power Operations Bulletin | Subject |
| --- | --- | --- |
| 11/11/2003 | ERCOT Power Operations Bulletin 53 | Revision to Day Ahead Desk |

# Security Alert Stage/ Threatcon/ Related issues

Security Threat Alert Yellow (Elevated) maintained through November.

OCN, Advisory, Alert, Emergency Notice and Major Events

11/12   Transmission Advisory for North – Houston. (15:20-17:45, 19:00 – 22:30)

11/17   Transmission Advisory for North – Houston. (06:27- 08:00)

Significant Communication Problems

11/11	 10:30 deployments held for upgrade to MMS.

11/21	Held 16:45 balancing deployments.   Study executed late due to problems with MOI.

11/26	Held 00:45 – 02:15 balancing deployments due to MOI not responding.

11/26	Held 02:45 – 03:15 balancing deployments due to MOI not responding.

## Major Computer Systems Problems/ Fixes

None.

# Major system Voltage problems

None.

Blackout/Load Shed incidents

Approximately 25 MW tripped during low frequency event 11/23 00:18.

ERCOT peak for last month (Unofficial)

11/3	38169

## Update on New Generation

No new generation made commercially available in the month of November.

## Max /MinTemperature

86 Nov 3rd, 21 Nov 24th (West)