| OGRR Number | 139OGRR | OGRR Title | Black Start Back Up Communication Facility Criteria |
| --- | --- | --- | --- |
| Recommended Action |  | Approve |  |
| Operating Guide Section Requiring Revision |  | 4A.1(b), Verifying Communications Adds new Section 4.6.5, Emergency Back Up Communication Facilities Criteria |  |
| Protocol Section Requiring Revision, if any. |  | ## 6.4.2, Determination of ERCOT Control Area Requirements, para (7) 6.5.8, Black Start Service |  |
| Proposed Effective Date |  | December 1, 2003 |  |
| Revision Description |  | Criteria for Emergency Back Up Communication Facilities Criteria |  |
| ###### Benefit |  | There was little or no specification in the Operating Guides for emergency back up communication facilities during a blackout. |  |
| OWG Recommendation |  | OWG recommended approval of OGRR139 as revised by OGRTF. |  |
| ROS Recommendation |  | ROS recommends approval of OGRR139 as revised by ROS. |  |
| PRS Consistency Determination |  | No PRS member noted a discrepancy between OGRR139 and the Protocols. |  |

| ## Sponsor |  |
| --- | --- |
| Name | Jack Thormahlen on behalf of the Black Start Task Force |
| E-mail Address | jthormahlen@lcra.org |
| Company | LCRA |
| Company Address | P.O. Box 220, Austin, Texas 78767 |
| Phone Number | 512-473-3200 ext. 2635 |
| Fax Number | 512-469-6856 |

Proposed Operating Guide Language Revision

Add a new subsection to Section 4

    - Emergency Back Up Communication Facilities Criteria

Reference:  Protocols Section 6.4.2

Black Start Service: ERCOT shall periodically determine and review the location and number of Black Start Resources required, as well as any special transmission or voice communication needs required. ERCOT and providers of this service shall meet the requirements as specified in the Operating Guides and in NERC policy.

All back up communications should have voice recording capabilities.  To prepare for a blackout event, any back up communications system shall meet the following minimum requirements:

1.	Be operational for 72 hours immediately following the start of a blackout without external power from the ERCOT grid;

2.	Provide direct voice communications between:  Black Start Resource and TO;

TO and appropriate TO; TO and ERCOT;

3.	Have written procedures that address operator training and the testing of the communication system; and,

4.	Comply with ERCOT communications standards in these Operating Guides.

In addition, public communications services, used for backup, must be limited to systems that are not oversubscribed.  Public communication services and dedicated lease lines must be available for 72 hours immediately following the start of a blackout without external power from the ERCOT grid.

4A.1	CONSIDERATIONS FOR SYSTEM RESTORATION

b.	Verifying Communications

Reliable communications will be the key to a safe and timely restoration following a collapse within the ERCOT System.  As part of the initial assessment after a partial or complete system collapse, communication facilities should be tested and verified.  It is possible, especially in case of a total ERCOT collapse, that communications with out-of-state QSEs may not be possible.  It is therefore critical that TOs and Generators located within their transmission system be able to communicate directly during these times.

The ERCOT System Operators should:

- Verify or establish communication paths with TOs.

- Verify or establish communications paths with QSEs.

- Verify integrity of ERCOT hotline.

- Periodically disseminate information to TOs and QSEs.

The TO operators should:

- Contact ERCOT in order to report status.

- Establish contact with Contracted Black Start Units and the Black Start Units’ QSE

- Initiate Black Start Plan

- Establish communication paths with other plants necessary to the restoration of the system in their area.

The QSE should:

- Contact ERCOT to report status of Generators within ERCOT

- Assist TOs as required.

- Ensure Generators are prepared to receive and follow instructions directly from the TO to which they are connected.

Should problems be encountered with any of the primary communication facilities, back up facilities shall be deployed and appropriate personnel notified.

Communications will be vital to an orderly recovery.  To keep communication facilities available, operating personnel should ensure that conversations are concise and effective.

| PRR Evaluation |  |
| --- | --- |
| Non-ERCOT Market Comparison | No Comparison conducted. |
| Comments Author | Comments Summary |
|  | None submitted |

| Sponsor's Revision Description | Criteria for Emergency Back Up Communication Facilities Criteria |
| --- | --- |
| ###### Sponsor's Reason for Revision | There was little or no specification in the Operating Guides for emergency back up communication facilities during a blackout. |