# Major Market Component

This paper describes the real-time operation of the ERCOT network using market products.

# Purpose

The purpose of Real-Time Operations is to economically dispatch resources in a reliable manner to match customer load, subject to generation and transmission constraints.  Real-Time Operations includes Security Constrained Economic Dispatch and Frequency Control, which together, govern the deployment of Balancing Energy, Regulation, and Responsive Reserve.

# Time Frame (Periodicity)

Security Constrained Economic Dispatch provides generator production set points and locational marginal prices (LMPs) every 5 minutes.  Load frequency control signals are provided for deployment of regulation resources and, when needed, responsive resources every 4 seconds.

# Definitions

##### Security-Constrained Economic Dispatch (SCED)– the determination of desirable generation outputs or other load Resource deployments using offer curves while considering state estimator output for load, Resources generation limits, actual transmission bus loads, and transmission constraints to provide the least-cost dispatch.

- Should there be a method to handle a load increment adjustment for rapidly changing loads (+/-) as well as self scheduled generation?

- Check whether other ISOs use load forecasts for 5-minutes SCEDs.

- How should SCED handle dispatch of units beyond offers to meet transmission constraints? [dispatching energy from reserve capacity]

- How will SCED handle uncontrollable units?

- How would portfolio dispatch of regulation interact with the determination of whether a unit can set the LMP? (bandwidth)

Load Frequency Control – deployment of those generation resources that are providing regulation service to ensure that system frequency is maintained within predetermined limits and deployment of those generation resources that are providing responsive reserve service when necessary as backup regulation. [Responsive Reserve on Loads will be deployed with a different algorithm.]

Responsive Reserve - daily operating reserves that are intended to 1) help restore the frequency of the interconnected transmission system within the first few seconds of an event that causes a significant frequency deviation; 2) provide energy during the implementation of the Emergency Electric Curtailment Plan (EECP); and 3) provide backup regulation. [Should responsive reserve on generation be expected to provide backup regulation?]

Regulation Energy – daily operating reserves that are intended to be deployed on 4second intervals to match load and generation with an acceptable system frequency.

State Estimator – defined in Security Analysis Paper

## Description

ERCOT's goal, during real time operations, is to match generation to load plus transmission losses in a SCED, which produces a least-cost dispatch subject to generation limits, actual transmission bus load, and transmission constraints, while maintaining system frequency in an acceptable manner.  To accomplish this goal, ERCOT will use two control strategies.  First, a SCED is produced by the Locational Marginal Price (LMP) calculator.  Second, frequency control is provided by Load Frequency Control (LFC), which attempts to reduce any system frequency deviations from scheduled frequency by providing a control signal for the use of those generation units committed to providing regulation and, when necessary, responsive reserve services.  In ERCOT, the SCED provided by the LMP Calculator will be updated ever 5 minutes, while the LFC will monitor system frequency and provide appropriate control signals to the QSEs every 4 seconds. These strategies are depicted in block diagram form in Figure 1.

These arrows are backward

The real time SCED for on-line generation in ERCOT is determined by the output of the LMP calculator as shown in Figure 2. The  LMP for each bus as determined by the LMP Calculator is posted to the ERCOT Information System every 5 minutes and is thus available to market participants for their use.

What are the Generating Unit Pricing Curves in the above figure? Loads providing Balancing Energy?

- Is there an arrow missing from the SE to the LMP preprocessor?

- Is a corrected LMP calculated ex post for settlement? (Advisory LMP is calculated ahead of time)

- Timing for components—LMP every 5 min, SE at least every 5 minutes, contingency processor runs approximately once per hour (or any time through dispatcher activation).  How many constraints are included in the contingency processor?

At the same time, the Bus LMPs and generator set points (or MW Base Points, using Figure 1 terminology) are also provided over an Inter-Control Center Protocol (ICCP) data link to the responsible QSE (refer to Figure 1).  The LMP Calculator produces a least-cost dispatch for the system's generation resources and dispatchable loads by minimizing the total system cost (which serves as the objective function) subject to actual transmission bus load and the constraints imposed by the transmission network (i.e., flow limits and N-1 contingencies) and the energy offers and physical limitations of each generation resource (i.e., generator minimum and maximum output and ramp rate(s)).  In other words, a SCED program is utilized within the LMP Calculator to perform an optimized least-cost dispatch that minimizes the least cost objective function (i.e., total system cost) subject to actual transmission bus load and the identified transmission and generation constraints.  [  Why specify solution here? ]

The rules for the assignment of offer curves to each generator are shown in Figure 3.

Do we want to specify price curves for the entire range of each resource? Not just prices for differential energy from a schedule

On right hand side: Change to Proxy offer curve

On left side, remove schedule (leave piecewise linear curve for physical resource)

In general, the LMP calculator uses the generators’ offer curves, unless ex-ante mitigation is active for a particular generator.  In this case, a market mitigation offer curve(s) is used for the non-competitive generator(s).  The LMP Calculator attempts to calculate a SCED using only generation for which it has offer curves.  Any generators that do not submit an offer curve (i.e., a "No Offer" unit in Figure 3) will be considered for dispatch by the LMP calculator only if there is no other solution possible.

Since the LMP Calculator's SCED moves generation up or down along its offer curve, there should be sufficient economic motivation such that generators will move their generation tothe SCED Base Points..  Consequently, it should not be necessary to directly penalize generation resources if they fail to follow SCED Base Points.  [How to determine whether a unit followed the Base Point and Regulation and Responsive deployments by ERCOT requires further discussion and remains to be determined.]   Address ex post calculation for settlement.  How to handle people not following price points?

ERCOT, based on network reliability need, has the authority to explicitly issue a dispatch order requiring a unit to move to a specific power output.  In this event, the unit is expected to respond to ERCOT’s dispatch instruction.  If the dispatch instruction requires the unit to move to its LMP set point, no additional compensation beyond normal settlement is provided.  If the dispatch instruction requires the unit to move to a power output other than its LMP set point, additional compensation may be provided to the responding unit.  [Needs additional thought on implementation]

The Load Frequency Controller (LFC) as shown in Figure 1 provides system frequency control based on the classic Area Control Error (ACE) algorithm:

ACE = (Scheduled Frequency minus actual Frequency in Hz) * (Frequency bias in MW/Hz)

- How does ERCOT calculate frequency bias?

The LFC receives input from real-time telemetry that includes generation output and system frequency. It also maintains a listing, along with unit status, of the generation capacity that is committed to provide regulation and responsive reserve services (refer to Figure 1).  Based on the ACE, the LFC issues a control signal over an ICCP data link or SCADA to each QSE that is proportional to its share of the aggregated capacity committed for regulation service.  QSEs are expected to distribute their regulation energy deployments according to the portion of regulation capacity awarded for each unit .  (more description is required)

In the event that all up regulation capacity has been deployed, the LFC package will issue dispatch control signals to the QSEs for responsive reserve deployment.  [I would rather see deployment of Responsive Reserve implemented by a separate system than LFC] (Performance monitor to assure that it is a rare event.  Monitor how regulation is deployed and used.  There is support for NERC CPS-1 as a criterion.)  However, because the LMP Calculator computes a new SCED based on a current State Estimator snapshot of system conditions, it is expected that regulation deployments will oscillate closely about a zero net energy deployment.  Consequently, deployment of reserve capacity in response to a full regulation capacity deployment is not expected to occur with any significant frequency.  In addition to governor response from  generation, LFC may issue reserve deployment signals when large deviations from system frequency occur as a result of generation trips or load variations.  [not fully convinced this should be automatic; have concerns about data validity and issuing large control actions based on potentially failed or flawed data] Finally, as discussed above, ERCOT Operations may deploy any on-line generation manually, if required to maintain system reliability.

# Inputs

For SCED :

- Actual generation by unit

- Actual transmission bus load

- Transmission network constraint limits (from security analysis)

- Offer curves

- Mitigation offer curves

- Generator operating constraints (minimum and maximum power outputs and ramp rates(s))

For Load Frequency Control:

- Frequency

- Scheduled Frequency

- Capacity available for regulation by QSE

- Participant’s percentage of capacity available for regulation

- Capacity available for responsive reserve by QSE

- Participant’s percentage of capacity available for responsive reserve

- System frequency bias

- Time error

- Control Area Bias

- Integrated ACE for approximately the last 5 minutes

# Outputs

For SCED:

- LMPs posted on the ERCOT website every 5 minutes

- Set points provided through data link (ICCP) or System Control and Data Acquisition (SCADA) for all online generation to each QSE

For Load Frequency Control:

- Regulation deployment signal provided through data link (ICCP) or SCADA to each QSE

- Responsive reserve deployment signal provided through data link (ICCP) or SCADA to each QSE

- Generating unit Participation factors for regulation

# Settlement

Payment to Generator = Generator Bus LMP x (Actual Energy Output in MWh – Scheduled Energy in MWh)

Where the LMP is calculated for the 15 minute settlement interval as the unit base point weighted average of the 5-minute LMPs that cover the settlement period (i.e. the sum of the products of the three 5 minute LMPs and the corresponding MW level for that LMP on its offer curve for the settlement period divided by the sum of those same MW levels equals the LMP Price for that settlement period)

Note – Scheduled Energy may be based on a bilateral or ERCOT auction contract or it may be zero if the unit is simply selling energy into the market.

#### Example

Assume

- The offer curve for the generator is composed of the following 3 points:

20 MW   -   $30

30 MW  -   $40

50 MW  -   $50

- The three 5-minute LMPs for the calculation intervals that cover a settlement interval for this generator bus are $30.00, $40.00 and $50.00 per MWh, respectively

- The generator base points in each of these calculation intervals are 20, 30 and 50 MW, respectively

- Actual generation energy =25 MWh

- Scheduled energy = 15 MWh

Then

Settlement LMP Price =  [(30*20) + (40*30) + (50*50)]/(20+30+50) = $43.00 per MWh

Excess energy payment for the settlement interval = 10 * $43.00 = $430.00

Methodology to be reviewed—compare other markets for settlement interval vs. dispatch interval and are the calcs weighted or not?