## Slide 1: Agreed Market Design Parameter for Vote at Future TNT Meeting January 13, 2004

## Slide 2: Real-Time Operations
LMP dispatch every 5 minutes with nodal prices and generator setpoints
LFC operating and moving regulation every 4 seconds
State estimator running approximately every 5 minutes just prior to SCED
State estimator provides load bus data and other network parameters to SCED (LMP calculator)
SCED (LMP calculator) will run every 5 minutes based on state estimator output, linearized binding constraints from security analysis, and history of area control error to remove error in load measurements.
Security analysis is run at least every hour or when major network topology changes to explore a prescribed set of contingencies on the then current network configuration to identify binding constraints and linearize their modeling for SCED. The number of linearized binding constraints should not be severely limiting (e.g., 100’s not 10’s)
  Dynamic line ratings will be supported by ERCOT for all TDSPs
  Settlement of imbalance energy will be done on a 15-minute interval based on the load weighted average of the LMPs calculated in the three 5-minute intervals
<number>

## Slide 3: Reliability Unit Commitment – Day Ahead
<number>
Run after close of day-ahead market and day-ahead ancillary services. Procurement should be run as early as possible on the day before – 12:00 noon or early afternoon.
Bilateral schedules will be entered by participants to reflect self-committed resources from ancillary services commitments, day-ahead market or bilateral transactions between participants.
ERCOT will perform the day-ahead RUC and will use its forecast of hourly load.
A security constrained unit commitment technique will be utilized.
The optimization of resources committed for the next day’s operation above those self-committed include the minimization of startup costs, no load operating costs, and minimum load energy costs subject to both transmission security constraints and reserve constraints. All units self-committed or still on line from previous days will have their energy bids set to zero for day-ahead RUC.

## Slide 4: Reliability Unit Commitment – Day Ahead
<number>
The output will be a list of units committed for tomorrow’s 24-hour operating period and the hours they need to be operational. It is assumed the units operate at minimum load unless instructed otherwise by the ERCOT dispatcher.
The resources committed will have a “make whole” provision where they will be guaranteed to earn at least their bids for the committed periods and minimum run times.
The costs to commit resources in day-ahead RUC after credits for market energy and net “make Whole” provisions will be assigned in general to those QSEs that did not self-commit resources for their obligations.
The costs to commit resources in day-ahead for local congestion will be monitored. A technique to assign any additional costs for local congestion may be developed and used in the future if practical.
(continued)

## Slide 5: Reliability Unit Commitment – Hour Ahead
<number>
Run every hour approximately one hour ahead of the operating period after the security analysis is run.
The run period will be for the operating hour period plus the remaining hours of the approved day-ahead RUCs (could be up to 35 hours).
The optimization of this RUC will be the same as the day-ahead RUC. All previously committed units will have their energy price set to zero.
ERCOT will update load forecasts during the day as required for the next 36 hours and input changes hourly for changes in unit outages and ratings, and transmission outages and ratings.
Resources needing commitment more than 6 hours ahead with startup times less than the time remaining until the resource is needed should be monitored and committed in a future hourly commit if the need still indicates.
Resources committed will have “make whole” provisions and the net costs associated with this RUC will be assigned to those QSEs short of capacity at the time of procurement.