## Slide 1: ERCOT Primary Frequency Control
Sydney L. Niemeyer
713-207-5051

## Slide 2: Primary Frequency Control Concerns
On average, one third of ERCOT’s Primary Control is supplied by Hydro Units
  These units respond only to large (negative) Hz deviations
Primary Hz Control to Frequency deviations less than +/- 0.1Hz averages 300 MW/0.1Hz.
Initial Primary Frequency Response is not maintained for entire event. (Proportionally to Hz deviation)
Initial Response droop has decayed.

## Slide 3: The 3 Interconnects at 06:00
January 20, 2004

## Slide 4: A 5% Droop unit in each Interconnect

## Slide 5: Western Interconnect

## Slide 6: Eastern Interconnect

## Slide 7: ERCOT Interconnect
3594 rpm
3600 rpm
3606 rpm

## Slide 8: Unit With Primary Control

## Slide 9: Unit Without Primary Control

## Slide 10: No Primary Control

## Slide 11: Oct 7, 2003
741 MW Trip

## Slide 12: Oct 31, 2003
392 MW trip

## Slide 13: Nov 23, 2003
585 MW trip
198 MW LaaR trip

## Slide 14: November 26, 2003
759 MW trip

## Slide 15: November 29, 2003
535 MW trip

## Slide 16: November 30, 2003
651 MW trip

## Slide 17: January 4, 2004
680 MW trip
175 MW LaaR Response

## Slide 18: January 22, 2004
218 MW unit trip
-0.06 Hz change
363.3 MW/0.1Hz Primary and Load Response, 295.0 MW/0.1Hz from turbines

## Slide 19: Responsive Reserve Units Only

## Slide 20: February 28, 1999

## Slide 21: April 1, 1999

## Slide 22: September 26, 1999

## Slide 23: November 4, 1999

## Slide 24: October 8, 2000

## Slide 25: November 17, 2000

## Slide 26: December 16, 2000

## Slide 27: January 21, 2001

## Slide 28: Summary
NERC and ERCOT Operating Guides
  Must have governor in service and free to respond.
  Maximum intentional governor dead band is +/-0.036 Hz.
Primary Frequency Control is vital for Interconnect Reliability