| PRR Number | 487PRR | PRR Title | Black Start Resources |
| --- | --- | --- | --- |
| Recommended Action |  | Approve as revised |  |
| Protocol Section(s) Requiring Revision (include Section No. and Title) |  | Section 6: Ancillary Services 6.1.8, Black Start Service 6.10.3.6, System Black Start Capability |  |
| Proposed Effective Date |  | Upon filling staffing requirements |  |
| Priority & Rank Assigned |  | N/A |  |
| Summary of Impact Analysis |  | No ERCOT computer system impacts; an additional 0.25 FTE is required to review and evaluate the proposals for Black Start Service in 2005; minor impacts to business procedures; impacts grid operations/practices. |  |
| Revision Description |  | Changes Black Start Ancillary Services language to allow an ERCOT Resource with a firm standby supply contract with an adjacent power pool supplier to bid as an ERCOT Black Start Resource. |  |
| Benefit |  | It will provide ERCOT with more and stronger Black Start Resources to restart the ERCOT grid under a complete blackout situation. Some ERCOT locations next to other power pools would have stronger alternates than the Resources that are currently allowed to bid. The adjacent power pools will be able to start larger ERCOT Resources and as such will enhance the restoration time from a complete blackout. |  |
| PRS Recommendation |  | PRS recommends approval of PRR487 as revised by STEC and ERCOT Comments. |  |

| Sponsor |  |
| --- | --- |
| Name | Dennis Kunkel |
| E-mail Address | dkkunkel@aep.com |
| Company | AEP |
| Company Address | 5502 Corporate Drive |
| Phone Number | 3612894003 |
| Fax Number | 3612894030 |

ERCOT/Market Segment Impacts and Benefits

|  | Impact |  | Benefit |
| --- | --- | --- | --- |
|  | Business | Computer Systems |  |
| ERCOT | More Selections | None | Additional Strong Black Start Resources to select from |
| MARKET SEGMENT | More Competition | None | None |
| Consumer | Possible faster restoration | None | Better value for the money |
| LSE: General, Including NOIE | None | None | None |
| LSE: CR & REP | None | None | None |
| QSE | More Resources able to bid | None | Faster restoration possible |
| Resource | More Resources able to bid | None | Faster restoration possible |
| TDSP | Faster Possible Restoration | None | Faster restoration possible |

Proposed Protocol Language Revision

{STEC Comments 021804}

### Black Start Service

As provided by ERCOT to QSEs: The procurement by ERCOT through Agreements, pursuant to emergency Dispatch by ERCOT and emergency restoration plans of Resources which are capable of self-starting or Resources within close proximity of another power pool which are capable of starting from such power pool via a firm standby power supply contract, without support from the ERCOT System, or transmission equipment in the ERCOT System in the event of a blackout, in order to begin restoration of the ERCOT System to a secure operating state.  Resources which can be started with a minimum of pre-coordinated switching operations using ERCOT transmission equipment within the ERCOT System may be considered for Black Start Service only where switching may be accomplished within one (1) hour or less.

As provided by a Generator or a QSE to ERCOT: The provision of Resources under a Black Start Agreement, pursuant to emergency Dispatch, which are capable of self-starting or Resources within close proximity of another power pool which are capable of starting from such power pool via a firm standby power supply contract, without support from the ERCOT System, or transmission equipment in the ERCOT System in the event of a blackout.  Resources which can be started with a minimum of pre-coordinated switching operations using ERCOT transmission equipment within the ERCOT System may be considered for Black Start Service only where switching may be accomplished within one (1) hour or less.

#### 6.10.3.6	System Black Start Capability

- Qualification will be provided to any Black Start Resource that has met the following requirements:

  - Verified control communication path performance;

  - Verified primary and alternate voice circuits for receipt of instructions;

  - Passed the basic starting test;

  - Passed the line energizing test;

  - Passed the Load carrying test;

  - Has started the next start unit, or has started the next start unit’s largest required motor and satisfied the next start unit’s minimum startup Load requirements; or has been demonstrated to the satisfaction of ERCOT staff through simulation studies conducted by the Black Start Service provider or a qualified third party, to be capable of starting the next start unit’s largest required motor while meeting the next start unit’s minimum startup Load requirements.  Potential Black Start Service bidders may request next start unit information from ERCOT prior to the selection process to satisfy this requirement.  ERCOT shall require this information from the designated next start unit as follows:  ERCOT may require any Generation Resource to provide largest motor startup information and unit startup energy requirements as needed to validate Black Start proposals or plans submitted by other Generation Resources.  Such data, if requested by ERCOT, shall be provided by the QSE representing the Generation Resource, or the Generation Resource Entity to ERCOT within thirty (30) days or less;

  - If not starting itself, has an ERCOT approved firm standby power contract with deliverability under ERCOT blackout circumstances from another power pool that can be finalized upon selection as a Black Start Resource;

  - If not starting itself, has an ERCOT approved agreement with the necessary TDSPs for access to another power pool , for coordination of switching during a Black Start event, for coordination of maintenance through the ERCOT Outage scheduler for all non-redundant transmission startup feeds; and

  - If dependent upon non-ERCOT transmission Resources, agreements providing this Transmission Service have been provided in the proposal.

- On successful demonstration of system Black Start Service capability, ERCOT shall qualify the Black Start Resource as being permitted to provide the system Black Start Service capacity and shall provide a copy of the certificate to the Black Start Resource.  Qualification shall be valid for one year from the date of the last successful Basic Starting test, three years from the date of the last successful line energizing test, or six years from the date of the last successful Load carrying test, whichever is earliest.  Qualification shall be revoked if the Black Start Resource fails to perform successfully during an actual restoration event, until the Black Start Resource is successfully retested.  Retesting is only required for the aspect of system Black Start Service capability (basic starting, line energizing, or Load carrying) for which the Black Start Resource failed.

  - Basic Starting Test

    - The basic ability of the Black Start Resource to start itself, or start from a normally open interconnection to another power pool, without support from the ERCOT System, is tested annually, either as a stand-alone test or part of the line energizing and Load carrying tests.  The test is run during a one-week period agreed on in advance by the Black Start Resource and ERCOT and must not cause  outage to ERCOT Customer Load or the availability of other Resources to the ERCOT market ;

    - ERCOT shall confirm the dates of the test with the Black Start Resource;

    - At a time during a previously agreed test week window not previously disclosed to the Black Start Resource, ERCOT will initiate the test;

    - The Black Start Resource, including all auxiliary Loads, will be isolated from the ERCOT power system, except for the transmission that connects the Resource to another power pool if the startup power is supplied by a firm standby contract.  Black Start Resources starting with the assistance of another power pool through a firm standby agreement will connect to the external grid, start-up, carry internal Load, disconnect from the external grid if not supplied through a black start capable DC Tie, and continue equivalently to what is required of other Black Start units;

    - The Black Start Resource will start without assistance from the ERCOT System, except for the transmission that connects the Resource to another power pool if the startup power is supplied by a firm standby contract;

    - The Black Start Resource must remain stable (in both frequency and voltage) while supplying only its own auxiliary Loads or Loads in the immediate area for at least thirty (30) minutes; and

    - The Black Start Resource must have verified that its Volts/Hz relay, over excitation limiter, and under excitation limiter are set properly and that no protection devices will trip the unit within the required reactive range.  Data to verify these settings will be provided to ERCOT.

| PRR Evaluation |  |
| --- | --- |
| Non-ERCOT Market Comparison | No Comparison conducted. |
| Comments Author | Comments Summary |
| Garland | Questions to the intent of ERCOT and the affects this PRR would have on priority conflicts and the process related to a system black out. Including, its contracts/agreements with black start power providers, i.e. D.C. Ties and the costs vs. savings to the Customer. |
| ERCOT | Revised language, also addresses Garland’s comments |
| STEC | Revised language and concerns |

| Sponsor's Revision Description | Changes Black Start Ancillary Services language to allow an ERCOT Resource with a firm standby supply contract with an adjacent power pool supplier to bid as an ERCOT Black Start Resource. |
| --- | --- |
| Sponsor's Reason for Revision | It will provide ERCOT with more and stronger Black Start Resources to restart the ERCOT grid under a complete blackout situation. Some ERCOT locations next to other power pools would have stronger alternates than the Resources that are currently allowed to bid. The adjacent power pools will be able to start larger ERCOT Resources and as such will enhance the restoration time from a complete blackout. |