| OGRR Number | 108-OGRR | OGRR Title | ERCOT REACTIVE STANDARDS |
| --- | --- | --- | --- |
| ###### Status |  | Posted |  |
| Operating Guide Section Requiring Revision |  | Part 2, addition of new section 2.13 |  |
| Protocol Section Requiring Revision, if any. |  |  |  |
| Requested Resolution |  | ## Add section 2.13 to the Operating Guide – Part 2 |  |
| Revision Description |  | Addition of ERCOT Reactive Standards to address minimum reactive capabilities of generating units - including cogenerators and self-serve generators, minimum reactive compensation at existing and future substations and minimum dynamic reactive reserve margins in the ERCOT electric network. |  |
| ###### Reason for Revision |  | Lack of Reactive Standards to address minimum reactive capabilities to assure voltage security in ERCOT network. |  |
| ## Sponsor |  |  |  |
| Name |  | Jose Conto |  |
| E-mail Address |  | jconto@ercot.com |  |
| Company |  | ERCOT |  |
| Company Address |  | 2705 West Lake Drive |  |
| Phone Number |  | 512-248-3141 |  |
| Fax Number |  | 512-248-3082 |  |
| ## Timeline |  |  |  |
| Date Received |  | 02/08/2002 |  |
| Date Posted |  | 02/08/2002 |  |
| ROS Review Date |  | 03/12/2002 |  |
| ROS Recommendation |  |  |  |
| Other Subcommittee Consideration |  |  |  |
| TAC Consideration |  |  |  |
| Board Consideration |  |  |  |

Proposed Operating Guide Language Revision

2.13	ERCOT REACTIVE STARDARDS

2.13.1	INTRODUCTION

ERCOT Reactive Standards aim to assure an acceptable level of voltage security within its network. Inadequate reactive power support from generation units, transmission lines and low load power factor correction expose the network to voltage instability or voltage collapse when additional disturbances or unusual increase in electric demand occur.

Static and dynamic reactive power resources are needed to supply the reactive power requirements of load demands and the reactive power losses in the electric systems, and provide adequate system voltage including both support and control.

Generators with operating right within ERCOT shall provide voltage and reactive support to the ERCOT system. TDSP’s shall maintain substation facilities at acceptable reactive compensation level.  ERCOT will establish the minimum reactive requirements to allow the electric system to operate within an acceptable voltage security level.

2.13.2	GENERATION ENTITY REACTIVE POWER REQUIREMENTS

Unless otherwise specifically approved by ERCOT, all existing and future generator installations shall have and maintain the following reactive capability at the generator's continuous rated power output:

- An overexcited power factor capability, measured at the generator terminals, of 0.9 or less leading and an underexcited power factor capability of 0.95 or less lagging (0.9 to –0.95); and

- An overexcited power factor capability, measured at the unit main transformer high voltage terminals (transmission voltage side), of 0.95 or less leading and an underexcited power factor capability of 0.95 or less lagging (0.95 to –0.95).

- The reactive capability required in 1 and 2 above must be maintained and available for utilization at all times the plant is on line.

- Each Generation Resource must be capable of maintaining a Voltage Profile limited to the quantity of Reactive Power the Generation Resource can produce at rated capability (MW) and a power factor of .95 leading or lagging measured at the unit main transformer high-voltage terminals. This quantity of Reactive Power is the Unit Reactive Limit (URL).

- Qualified renewable generators (as described in Section 14, Renewable Energy Credit Trading Program) and Generation Resources in operation prior to September 1, 1999, whose current design does not allow them to meet the URL as stated above, will be required to maintain a Voltage Profile that is limited to the quantity of reactive power that the Generation Resource can produce at its rated capability (MW) using procedures and criteria as described in the Operating Guides.

- Each Generation Resource is expected to be compliant with the Operating Guides for response to transient voltage disturbance.

- Each Generation Resource providing Voltage Support Service {Is this a defined term?} must meet technical requirements specified in the Ancillary Service Qualification, Testing and Performance Standards section of the ERCOT Protocols, Section 6.10.

- Each Generation Resource shall operate with the unit’s automatic voltage regulator (AVR) and Power System Stabilizers (PSS) in use unless specifically directed to operate in manual mode by ERCOT, or unless the QSE determines a need to operate in manual in emergency conditions.  When the QSE changes the mode, the QSE shall promptly inform ERCOT.   QSEs’ control centers will continuously monitor the status of their regulators and stabilizers.

- Units must remain connected during the following conditions, unless equipment damage will result:

  - Frequency conditions as detailed in Section 3.2.4.6 of the ERCOT Operating Guides

  - Generator terminal voltages that are within 5 % of the rated nominal design voltage.

  - Generator terminal voltage deviations that exceed 5% but are within 10% of the rated nominal design voltage and persist for less than 10.0 seconds.

  - Generator volts per hertz conditions that are less than 116% (of generator nominal voltage) that last for less than 1.5 seconds.

  - Fault (three-phase, single-phase or phase-to-phase) cleared by the primary protection scheme (i.e., no failure of protective devices or transmission breakers) on any line connected to the generator’s transmission interconnect bus.

- Overexcitation limiters, when used, shall be coordinated with the thermal capability of the generator field winding and protective relays in order to permit short-term reactive capability that allows at least 80% of the unit design standard (ANSI C50.13-1989), as follows:

Time (seconds)	10	30	60	120

Field Voltage %	208	146	125	112

- After allowing temporary field current overload, the limiter shall operate through the AVR to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The overexcitation limiter shall be coordinated with the over-excitation protection so that overexcitation protection only operates for failure of the voltage regulator/limiter.

- All generation facilities with unit nameplate ratings greater than 20 MVA shall meet these requirements or obtain a specific exemption approved by ERCOT.  {Question: Are these standards limited to generators directly connected to the transmission system (60kv and above)?  If so, then what are the standards for generators directly connected to distribution systems?  }

- Any short-term inability of a generator to meet these minimum reactive requirements shall be immediately reported to ERCOT by the Generating Entity (GE).  Any long-term changes to this information must be provided to ERCOT by the GE within 60 days as changes or upgrades are made during the life of the plant.

- Within 30 days of ERCOT’s request, GE shall provide ERCOT with the operating characteristics of any generator’s equipment PRS (define?) or controls that may respond to temporary excursions in voltage, frequency, or loading with actions that could lead to tripping of the generator.

High reactive loading and reactive oscillations on generation units should be immediately communicated to ERCOT by the GE.  GE’s SHALL NOT reduce high reactive loading on individual units without instructions from ERCOT and the QSE.  High reactive loading and/or reactive oscillations are a possible indication of voltage instability.  Operator action to reduce this loading may aggravate a voltage stability problem that may lead to voltage collapse.

Unit tripping off line due to voltage or reactive problems should be immediately reported to ERCOT and the QSE.  These tripping events should be thoroughly investigated by the generation entity along with the TDSP and ERCOT.  The ERCOT Power Dynamic Committee Working Group should monitor and investigate these tripping events and report results to ROS.

If specifically approved by ERCOT, a generating unit may be exempted from these requirements; however, if such an exemption is approved, the GE must make alternate arrangements for supplying an equivalent dynamic reactive power capability as necessary to meet the area’s reactive power requirements.  All exemptions granted are subject to future ERCOT review as conditions change.  {Question:  Should the GE provide projected reactive power output from the generator through the QSE or directly with ERCOT?  Is it a requirement that the GE provide real time VARS output to ERCOT?  We need to check the Protocols.}

2.13.3	COGENERATOR AND SELF-SERVE GENERATOR REQUIREMENTS

A cogenerator or self-serve generator with internal electric load supplying power to the transmission grid shall meet the same requirements as a generator for that portion of power supplied to the transmission grid.  Measurement will be effectively at the transmission point where the generator’s high side protective device connects to the transmission system of the TDSP.

{Question:  Are provisions needed in these guidelines to set minimum standards for monitoring devices to measure reactive power flows from any generator into the transmission grid?  }

2.13.4	TRANSMISSION AND DISTRIBUTION SERVICE PROVIDER (TDSP) REACTIVE POWER REQUIREMENTS

Unless otherwise specifically approved by ERCOT, the TDSPs at every existing and future substation shall have and maintain during the peak summer months the following reactive compensation:

- A power factor of 0.95 or greater anytime substation load is greater than or equal to 80% of projected substation peak demand, measured at the substation transformer high voltage terminals; and

- A power factor of 0.93 or greater anytime substation load is less than 80% of projected substation peak demand, measured at the substation transformer high voltage terminals

If the substation has multiple transformers, the real and reactive load along with transformer reactive losses served by each transformer may be added together when calculating the substation power factor.

If specifically approved by ERCOT, the TDSPs may aggregate distribution substations in a local area or on a radial line to quantify the obligation for supplying equivalent reactive power compensation to meet the area’s reactive power requirements.

If specifically directed by ERCOT, TDSPs may be required to exceed these requirements as necessary to meet the area’s reactive power requirements to maintain voltage as long as the TDSP has determine that the additional requirements are not detrimental to the operations of the TDSP system and as long as sufficient notification has been provided by ERCOT to the TDSP.  In addition, in some areas of ERCOT during light load conditions, a lower power factor requirement (0.92 or less) may be directed by ERCOT to keep voltages within acceptable operating limits.  ERCOT’s notification will be base on manual switching instructions to the TDSP.  If response time for manual operations is not adequate then the TDSP will be given time by ERCOT for the TDSP to install remote control facilities to improve the response time.

ERCOT directs the TDSPs at every existing and future substation in the following counties to achieve and maintain a power factor of 0.98 or greater anytime substation load is greater than or equal to 80% of projected substation peak demand during the peak summer months, measured at the substation transformer high voltage terminals:

| Dallas-Ft. Worth Area | Dallas County Denton County Ellis County Hood County Hunt County Kaufman County Johnson County Parker County Rockwall County Tarrant County Wise County Collin County |
| --- | --- |
| Rio Grande Valley Area | Hidalgo County Cameron County |
| Laredo Area | Webb County |
| Austin/Round Rock Area | Travis County Williamson County |
| San Angelo Area | Tom Green County |
| Bryan/College Station Area | Brazos County |
| Houston Area | Harris County Chambers County Brazoria County Galveston County |

Any short-term inability to meet these minimum reactive requirements shall be immediately reported to ERCOT.  Any long-term changes to this reactive requirement must be provided to ERCOT at least 60 days before changes or upgrades over the life of the substation.

If specifically approved by ERCOT, a TDSP may be exempted from this requirement; however, if such an exemption is approved, the TDSP must make alternate arrangements for supplying equivalent reactive power compensation as necessary to meet the area’s reactive power requirements.  All exemptions granted are subject to future ERCOT review as conditions change but with the understanding ERCOT with provide sufficient time to allow the TDSP to budget, design, purchase, and install additional power factor correction facilities.

{Comment:  We have concerns about associated costs with ERCOT directives related to reactive power factor facilities.  We need to have certainty in these standards that ERCOT will support TDSP TCOS filing to the PUCT if the directive by ERCOT, or ERCOT approval, requires the TDSP to install reactive power factor correction facilities on the low side of a delivery substation.  Subsequently, the following language is suggested:}

It the process of preparing and adopting, by the ERCOT stakeholders, these guidelines related to reactive standards, it is understood that TDSPs may exercise provisions in the PUCT Substantive Rule that states specify capacitors and other reactive devices are deemed to be transmission cost of service (TCOS) facilities and subject to transmission cost of service recovery if such related costs meet the conditions in PUCT Substantive Rules 25.192(C)(1)(D).  Furthermore, it is understood that ERCOT will support the TDSP TCOS filing for such facilities that are directed or approved by the ERCOT planning staff.  The principle supporting the recovery of such facilities through TCOS is based on the fact that capacitors and other reactive devices that are needed to support the transmission system may not necessarily be required to support or optimize the operation of the DSP’s distribution system, served from delivery substations connected to the ERCOT transmission grid.

{Comment:  In the Interim Reactive Standards, a provision was included that would allowed TDSPs to gradually meet over several years augmented power factor levels at delivery substations in certain counties connected to the ERCOT transmission grid.  It appears these proposed standards do not have any phased-in time frame.  TDSPs must be given sufficient time to budget, design, purchase, and install capacitors.  Subsequently, these standards need to include acceptable timetables to meet targeted power factor levels.}

{Comment:  These standards do not address monitoring and compliance measures.  Some entities have VAR metering facilities with interval data already in place; whereas, other entities have facilities with limited capabilities or no facilities installed at this time.  ERCOT should adopt measures that treat all entities equally when monitoring loads to meet reactive standards.}

2.13.5	DYNAMIC REACTIVE RESERVE PLANNING REQUIREMENTS

The transmission system will be planned and enough reactive compensation (both dynamic and static) will be installed and maintained to keep a 20% dynamic reactive reserve margin (both overexcited and underexcited dynamic reactive capability) on generation units within geographic areas defined by ERCOT.  This planning requirement will apply under normal conditions and following any Category B or C contingency as defined in the ERCOT Planning Criteria.

The dynamic reactive reserve percentage in a local area is calculated by the following formula:

100*(LARC - LARS)/ LARD

Where:

LARC = Total local area available dynamic reactive capability

LARS = Total local area reactive supplied from dynamic sources

LARD = Total local area reactive load + total local area reactive losses

(As calculated from power flow, normal and contingency conditions)

{Questions: Define local?  Will ERCOT be responsible for notifying the TDSP of the location and amount of dynamic reactive margin to be installed?  Will the pending voltage reactive study impact the proposed 20% of dynamic reactive correction?}

2.13.6	ERCOT AND NERC REQUIREMENTS

The generation entity, distribution service provider, and transmission service provider must comply with all applicable ERCOT and NERC requirements, including, without limitation, those contained in the ERCOT Operating Guides, ERCOT Protocols, ERCOT Planning Criteria, NERC Operating Manual, and NERC Planning Standards.  It is understood and agreed that such requirements are subject to change from time to time, and such changes shall automatically become applicable upon the effective date of the approved change.

{Question:  What are the consequences for not upholding these proposed standards for both GEs and TDSPs?}

{Question:  What is the targeted timetable for entities to meet the proposed standard if approved?}

{Comment and Question: There seems to be overlapping reliability, operational and commercial issues that may need to be addressed jointly with WMS and RMS.  For example, if ERCOT determines that additional VARS are needed from a generator in a specify area of the system to provide voltage support, what is the form of compensation (if any) specially if the GE must reduce MW output to provide the additional VARS to support the transmission grid?  Since VARS are local in nature, it initially appears a viable market solution may not be practical.}

| ## Other TAC Subcommittee Review |  |
| --- | --- |
| PRS Review Date |  |
| PRS Protocols Impact Decision |  |
| WMS Review Date |  |
| RMS Review Date |  |
| ## TAC Action |  |
| TAC Vote Date |  |
| TAC Proposed Implementation Date |  |
| TAC Vote Results |  |
| ## ERCOT Board Action |  |
| ERCOT Board Vote Date |  |
| ERCOT Board Implementation Date |  |
| ERCOT Board Results |  |
| ## Appeal |  |
| Appeal Date |  |
| Entity Initiating Appeal |  |
| Nature of Appeal |  |