| OGRR Number | 138OGRR | OGRR Title | Generator Reactive Design Curves – Submission to ERCOT |
| --- | --- | --- | --- |
| ###### Date |  | August 15, 2003 |  |
| ## Submitter’s Information |  |  |  |
| Name |  | Wayne Kemper |  |
| E-mail Address |  | Wayne.kemper@centerpointenergy.com |  |
| Company |  | CenterPoint Energy |  |
| Company Address |  | P.O. Box 1700, Houston Texas 77251 |  |
| Phone Number |  | 713-207-2192 |  |
| Fax Number |  | 713-207-2444 |  |

The first change, shown below, is to clarify how normal switchyard voltage is to be maintained. Additionally, ERCOT should consider allowing some percent deviation from normal switchyard voltage during a test to maximize test performance. The second change is to verify if the test is performed with the AVR in service.

Proposed Operating Guide Language Revision

### 6.2.3	Biennial Unit Reactive Limits (Lead and Lag) Verification

General Information

Unit Code (16 character):   			Location (County) :

Unit Name:  					Date of test:

Generator’s QSE:  				Resource Entity:

Test Details

Instructions:

Maximum lagging reactive tests should be performed with the unit at its net dependable MW capability.  Leading reactive tests are to be performed during light load conditions of the ERCOT System.  Maximum lagging reactive tests are to be performed during ERCOT System high load conditions.  This form is to be submitted to ERCOT..  Inability to reach the design limit must be noted with an explanation of the limiting factor, which prevented design performance.  Verify that the automatic voltage regulator is in service.  Minimum acceptable test duration is 15 minutes.  The normally specified switchyard voltage should be maintained by adjusting voltage control devices/units (other than the unit under test)  in so far as possible.  Show leading reactive value as a negative (-) number.

Generator Reactive Design Curves are to be submitted to ERCOT along with, or prior to, the initial Reactive Limit Test results, or any time a design change for a unit occurs which causes a Design Curve change.  ERCOT will maintain a file of Generator Reactive Design Curves for reference.

## MACHINE DESIGN CAPABILITY

Leading Reactive at Minimum Design MW Output	________ MVAR

Lagging Reactive at Maximum Design MW Output	________ MVAR

Test Performed:				Location at which data observed:

 Maximum Leading Reactive		 Generator Terminals (preferred)

 Maximum Lagging Reactive		 High Voltage side of Generator Step-Up (GSU) Transformer

 Other (specify location):

TESTED REACTIVE CAPABILITY

Generator Gross Reactive (MVAR): (+/-) _____ Net Reactive to System (MVAR): (+/-) _____

Auxiliary Reactive Load (MVAR): _____ (if available)

TEST CONDITIONS:

Start Time: ________________	Stop Time: ______________

Generator Gross Generation (MW): _____	Net Dependable Unit Generation (MW): _____

Auxiliary Load (MW): _____			Power Factor: _____

Transmission Bus Voltage (kV): _____	Nominal Transmission Bus Voltage (kV): _____

Generator Terminal Voltage (kV): _____	Auxiliary Bus Voltage (kV): _____ (if limiting)

Ambient Air Temperature (°F): _____

Generator Hydrogen Pressure (psi): _____

Automatic Voltage Regulator In Service (Yes or No)   _   _______

Generator Step Up transformer tap setting: ______   Ratio: HV _______ kV/ LV ________kV

Abnormal Conditions at Time of Test:

Factors that Limited Reactive Capability During Test:

 Maximum Generator Voltage with Auxiliary loads		 Steady State Stability Limit

 Maximum Generator Voltage without Auxiliary loads	 Maximum Gross MW capability

 Minimum Generator Voltage with Auxiliary loads		 Minimum Gross MW capability

 Minimum Generator Voltage without Auxiliary loads	 Minimum Excitation Limiter

 Main transformer capability plus Auxiliary loads		 Loss of Field Relay

 Other:

Submittal

Resource Entity Representative:

QSE Representative:

Date submitted to ERCOT Control Area Authority Rep.:

Notes:	1.  Leading and Maximum Lagging tests may be conducted at different times of the year.

| ## Other TAC Subcommittee Review |  |
| --- | --- |
| PRS Review Date |  |
| PRS Protocols Impact Decision |  |
| WMS Review Date |  |
| RMS Review Date |  |
| ## TAC Action |  |
| TAC Vote Date |  |
| TAC Proposed Implementation Date |  |
| TAC Vote Results |  |
| ## ERCOT Board Action |  |
| ERCOT Board Vote Date |  |
| ERCOT Board Implementation Date |  |
| ERCOT Board Results |  |
| ## Appeal |  |
| Appeal Date |  |
| Entity Initiating Appeal |  |
| Nature of Appeal |  |