| OGRR Number | 138OGRR | OGRR Title | Generator Reactive Design Curves – Submission to ERCOT |
| --- | --- | --- | --- |
| Recommended Action |  | Approve |  |
| Proposed Effective Date |  | December 1, 2003 |  |
| Operating Guide Section Requiring Revision |  | 6.2.3, Biennial Unit Reactive Limits (Lead and Lag) Verification |  |
| Protocol Section Requiring Revision, if any. |  | None |  |
| ###### Revision Description |  | Clarifies and improves reactive limit verification form. |  |
| ###### Benefit |  | Clarifies and improves reactive limit verification form. |  |
| OWG Recommendation |  | OWG recommends approval of OGRR138 as modified by OGRTF. |  |

| ## Sponsor |  |
| --- | --- |
| Name | Tom Peterson |
| E-mail Address | Tom.peterson@txu.com |
| Company | TXU Portfolio Management Company, LP (QSE) |
| Company Address | 1717 Main Street, Dallas, TX 75201 |
| Phone Number | 214-875-9299 |
| Fax Number | 214-875-9069 |

Proposed Operating Guide Language Revision

These comments /changes are to better specify and clarify the design test points and define “Net Reactive to System (MVAR): (+/-)”

### 6.2.3	Biennial Unit Reactive Limits (Lead and Lag) Verification

General Information

Unit Code (16 character):   			Location (County) :

Unit Name:  					Date of test:

Generator’s QSE:  				Resource Entity:

Test Details

Instructions:

Maximum lagging reactive tests should be performed with the unit at its net dependable MW capability. Maximum leading reactive tests should be performed with the unit at its net minimum dependable MW capability. Leading reactive tests are to be performed during light load conditions of the ERCOT System.  Maximum lagging reactive tests are to be performed during ERCOT System high load conditions. (Note 1)  This form is to be submitted to ERCOT.. with a copy of the generator reactive design curve, marking the measured maximum output.  Inability to reach the design limit must be noted with an explanation of the limiting factor, which prevented design performance.  Verify that the Automatic Voltage Regulator is in service.  Minimum acceptable test duration is 15 minutes.  The normally specified switchyard voltage should be maintained by adjusting voltage control devices/units (other than the unit under test) in so far as possible.  Show leading reactive value as a negative (-) number.

## MACHINE DESIGN CAPABILITY

Leading Reactive at Minimum Design MW Output	________ MVARs at _________MWs

Lagging Reactive at Maximum Design MW Output	________ MVARs at _________MWs

Test Performed:				Location at which data observed:

 Maximum Leading Reactive		 Generator Terminals (preferred)

 Maximum Lagging Reactive		 High Voltage side of Generator Step-Up (GSU) Transformer

 Other (specify location):

TESTED REACTIVE CAPABILITY

Generator Gross Reactive (MVAR): (+/-) _____

Net Reactive to System (MVAR): (+/-) (Note 2) _____

Auxiliary Reactive Load (MVAR): _____ (if available)

Load Host Reactive (MVAR): (Note 3)_____ (if applicable)

TEST CONDITIONS:

Start Time: ________________	Stop Time: ______________

Generator Gross Generation (MW): _____	Net Dependable Unit Generation (MW): _____

Auxiliary Load (MW): _____			Generator Terminal Power Factor: _____

Transmission Bus Voltage (kV): _____	Nominal Transmission Bus Voltage (kV): _____

Generator Terminal Voltage (kV): _____	Auxiliary Bus Voltage (kV): _____ (if limiting)

Ambient Air Temperature (°F): _____

Generator Hydrogen Pressure (psi): _____

Automatic Voltage Regulator in service as required (Yes or No)   _   _______

Generator Step Up transformer tap setting: ______   Ratio: HV _______ kV/ LV ________kV

Abnormal Conditions at Time of Test:

Factors that Limited Reactive Capability During Test:

 Maximum Generator Voltage with Auxiliary loads		 Steady State Stability Limit

 Maximum Generator Voltage without Auxiliary loads	 Maximum Gross MW capability

 Minimum Generator Voltage with Auxiliary loads		 Minimum Gross MW capability

 Minimum Generator Voltage without Auxiliary loads	 Minimum Excitation Limiter

 Main transformer capability plus Auxiliary loads		 Loss of Field Relay

 Other:

Submittal

Resource Entity Representative:

QSE Representative:

Date submitted to ERCOT Control Area Authority Rep.:

Notes:	1.  Leading and Maximum Lagging tests may be conducted at different times of the year.

2. Net Reactive to System (MVAR): (+/-) is calculated as Gross generation reactive minus Auxiliary reactive load minus Generator step up transformer reactive losses minus Load host reactive

Net Reactive = 	Gross generation reactive – (Auxiliary reactive load +
Generator step-up transformer reactive losses + Load host reactive)

3.  Load Host Reactive data required when testing a private network and/or self-serve generator

| Comments Author | Comments Summary |
| --- | --- |
| LCRA | Revised language. |
| CenterPoint | Revised language. |

| Sponsor's Revision Description | Remove the requirement that Generator Reactive Design Curves be submitted to ERCOT each time that a Reactive Limit Test is performed and submitted. |
| --- | --- |
| ###### Sponsor's Reason for Revision | Generator Reactive Design Curves are static in nature, and therefore need only be provided to ERCOT along with, or prior to, the initial Unit Reactive Limit Test results. |