| OGRR Number | 149OGRR | OGRR Title | Types of Responsive Reserve |
| --- | --- | --- | --- |
| ###### Date |  | May 18, 2004 |  |
| ## Submitter’s Information |  |  |  |
| Name |  | David A. Darnell, on behalf of OGRTF |  |
| E-mail Address |  | dadarnell@cps-ems.com |  |
| Company |  | City Public Service of San Antonio |  |
| Company Address |  | PO Box 1771, San Antonio, TX 78296-1771 |  |
| Phone Number |  | 210-353-2208 |  |
| Fax Number |  |  |  |

Comments

The changes below reflect revisions made at the 5/18 OGRTF meeting.

Revised Proposed Operating Guide Language

#### 2.5.2.3	Types Of Responsive Reserve

Reference:  Protocols Section 6.5.4, Responsive Reserve Service

Responsive Reserve Service (RRS) may be provided by:  (a) Unloaded Generation Resources that are On-line; (b) Resources controlled by high-set under-frequency relays; (c) Hydro Responsive Reserves; or (d) From DC Tie response that stops frequency decay.  The minimum amount of RRS provided by Generation Resources shall be as specified in the Operating Guides.  QSE’s Generation Resources providing RRS must be On-line and capable of ramping to the awarded output level within ten (10) minutes of the notice to deploy energy, must be immediately responsive to system frequency, and must be able to maintain the scheduled level for the period of service commitment.  The amount of RRS on an individual Generation Resource may be further limited by requirements of the Operating Guides.

Responsive reserves provided by a QSE shall meet the following requirements:

- (1)	In no case shall more than twenty percent (20%) of the Net Dependable Capability for any non-Combined Cycle thermal unit be used as Responsive Reserve.

- (2)	In no case shall more than twenty percent (20%) of the combined Net Dependable Capability for any Combined Cycle Block with one or more CTs or GTs coupled to a Steam Turbine, with their net maximum capability aggregated together, be used as Responsive Reserve.

- (3)	In no case shall more than twenty percent (20%) of the Net Dependable Capability for any hydro unit with a five percent (5%) droop setting operating as a generator be used as Responsive Reserve.