| PRR Number | 468PRR | PRR Title | Frequency Response Requirements and Monitoring |
| --- | --- | --- | --- |
| Protocol Section(s) Requiring Revision (include Section No. and Title) |  | Section 5.8, Frequency Response Requirements and Compliance Monitoring [New] |  |
| Effective Date |  | June 1, 2004 |  |
| Priority & Rank Assigned |  | N/A |  |
| Summary of Impact Analysis |  | No impact to ERCOT computer systems; minor staffing impacts (0.25 FTE for Compliance to design and administer appropriate performance monitoring and scoring methods); minor impacts to business functions and grid operations/practices. |  |
| Revision Description |  | Adds Section 5.8, establishing requirements for Generation Resource governor response, and establishing performance monitoring and reporting criteria. |  |
| Benefit |  | To ensure that the expected state of the system will be secure in the face of unexpected events, Generation Resource governor response, proportional to the frequency error, applied dynamically in seconds without Dispatch Instruction from ERCOT, is essential. Although mentioned in the ERCOT Operating Guides, existing Protocols are silent as to the obligation to maintain governors in service, and to respond to frequency excursions. This PRR is needed to ensure such response continues to be available to the system, limiting frequency error, and maintaining reliability. |  |
| PRS Recommendation |  | PRS recommends approval of PRR468 as revised by ROS-WMS Task Force comments dated 01/22/04, ERCOT comments dated 02/16/04, and PRS. |  |
| TAC Recommendation |  | After voting to declare PRR468 urgent, TAC recommends approval of PRR468 as revised by TAC. |  |
| Board Action |  | Board approved PRR468 as recommended by TAC. |  |

| Sponsor |  |
| --- | --- |
| Name | Fred Sherman (on behalf of the Reliability and Operations Subcommittee) |
| E-mail Address | fsherman@ci.garland.tx.us |
| Company | Garland Power & Light |
| Company Address |  |
| Phone Number |  |
| Fax Number |  |

Proposed Protocol Language Revision

{ERCOT Comments 021604, PRS, and TAC revisions}

(The following shall be added to Section 5 of the Protocols)

## 5.8	Frequency Response Requirements and  Monitoring

### 5.8.1	Generation Resource and QSE Participation

#### 5.8.1.1	Governor in Service

At all times a Generation Resource is on line, its turbine governor shall remain in service and be allowed to respond to all changes in system frequency.  Generation Entities shall not reduce governor response on individual Resources during abnormal conditions without ERCOT’s consent (conveyed by way of the Generation Entity’s QSE) unless equipment damage is imminent.

#### 5.8.1.2	Reporting

Generation Entities shall conduct applicable generating governor speed regulation tests on Resources as specified in the Operating Guides.  Test results and/or other relevant information shall be reported to ERCOT and ERCOT shall forward results to the appropriate TSPs.

Resource governor modeling information required in the ERCOT Planning Criteria shall be determined from actual Resource testing described in the Operating Guides.  Within thirty (30) days of ERCOT’s request, the results of the latest test performed shall be supplied to ERCOT and the connected TSP.

When the governor of a Generation Resource is blocked while the Resource is operating, the QSE shall promptly inform ERCOT.  The QSE shall also supply governor status logs to ERCOT upon request.

Any short-term inability of a Generation Resource to supply governor response shall be immediately reported to ERCOT.

If a Generation Resource trips Off -line due to governor response problems, the Generation Entity shall immediately report the change in the status of the Resource to ERCOT and the QSE.

### 5.8.2	Primary Frequency Control Measurements

For the purposes of this section, the A Point is the last stable frequency value prior to a frequency disturbance.  For a decreasing frequency event with the last stable frequency value of 60.000 Hz or below, the actual frequency is used.  For a decreasing frequency event with the last stable frequency value between 60.000 and 60.036 Hz, 60.000 Hz will be used.  For a decreasing frequency event with the last stable frequency value above 60.036 Hz, actual frequency will be used.  For an increasing frequency event with the last stable frequency value of 60.000 or above, the actual frequency is used.  For an increasing frequency event with the last stable frequency between 59.964 and 60.000 Hz, 60.000 Hz will be used.  For an increasing frequency event with the last stable frequency value of 59.964 or below, the actual frequency is used.  ERCOT shall determine the A Point frequency for each event.

For the purposes of this section, the C Point is the lowest frequency value during the first five   seconds of the event.

For the purposes of this section, the B Point is the “recovery” frequency value after the C Point.   The B Point should occur after full governor response of the turbines has occurred, usually between ten (10) and thirty (30) seconds after the A Point, but not greater than sixty (60) seconds after the A Point.  ERCOT shall determine the B Point for each event.

B Point Plus Thirty Seconds: At thirty seconds following the B Point, an analysis will be performed by ERCOT with the assistance of the appropriate ERCOT subcommittee to determine if primary frequency control response is sustained.

For the purposes of this section, a “Measurable Event” is the sudden change in interconnection frequency that will be evaluated for performance compliance will have i) a frequency B Point between 59.700 Hz and 59.900 Hz or between 60.100 Hz and 60.300 Hz, and ii) a difference between the B Point and the A Point greater than or equal to +/- 0.100 Hz.

#### 5.8.2.1	ERCOT Required Primary Frequency Control Response

The combined response of all Generation Resources interconnected in ERCOT to a Measurable Event shall be at least 420 MW / 0.1 Hz. This value should be reviewed on an annual basis by ERCOT and the appropriate ERCOT subcommittee for system interconnect reliability needs.

ERCOT will evaluate, with the assistance of the appropriate ERCOT subcommittee,  primary frequency control response during Measurable Events.  The actual Generation Resource response will be compiled to determine if adequate primary frequency control participation was available.

ERCOT and the appropriate ERCOT subcommittee will review each Measurable Event, verifying the reasonableness of data.  Data that is in question may be requested from the QSE for comparison and/or individual Resource data may be retrieved from ERCOT’s database.

ERCOT’s performance will be averaged using the most recent six (6) Measurable Events to determine its rolling average contribution.

#### 5.8.2.2

- .

### 5.8.3	ERCOT Data Collection

#### 5.8.3.1	Data Collection

ERCOT will collect all data necessary to analyze each Measurable Event.  This will include the following real-time  data:

- Interconnection Frequency;

- Regulation Service deployed;

- Responsive Reserve Service deployed;

- QSE available  Responsive Reserve Service;

- QSE total Generation;

- QSE SCE;

- QSE Bias;

- QSE LaaR MW;

- LaaR deployed;

- QSE Responsive Reserve Service; and,

- ERCOT Load and individual Resource(s) that contributed to the frequency deviation.

| PRR Evaluation |  |
| --- | --- |
| Non-ERCOT Market Comparison | No Comparison conducted. |
| Comments Author | Comments Summary |
| Calpine | Agrees with 468PRR. |
| Oncor | Discusses conflicts between PRR and Operating Guides. |
| TXU | Agrees but has questions and feels it conflicts with existing Protocol language. |
| STEC/MEC | Has revisions. |
| ERCOT 1/21/04 | Recommends revisions. |
| ERCOT 2/17/04 | Recommends revisions for clarification and conformance to the Protocols. |

| Sponsor's Revision Description | Adds Section 5.8, establishing requirements for QSE portfolio generator governor response, and establishing performance monitoring criteria. |
| --- | --- |
| Sponsor's Reason for Revision | To ensure that the expected state of the system will be secure in the face of unexpected events, generator governor response, proportional to the frequency error, applied dynamically in seconds without Dispatch Instruction from ERCOT, is essential. Although mentioned in the ERCOT Operating Guides, existing Protocols are silent as to the obligation to maintain governors in service, and to respond to frequency excursions. This PRR is needed to ensure such response continues to be available to the system, limiting frequency error, and maintaining reliability. |