| OGRR Number | 150OGRR | OGRR Title | Clarification to UF Relay Trip Time for Load Shedding |
| --- | --- | --- | --- |
| Operating Guide Section Requiring Revision |  | 1.5, Conformance to NERC Policies and Procedures |  |
| Protocol Section Requiring Revision, if any. |  | ## None |  |
| Requested Resolution |  | ## Normal |  |
| Revision Description |  | ## Clarification to UF relay trip time for load shedding |  |
| ###### Reason for Revision |  | Clarification to UF relay trip time for load shedding |  |
| Timeline |  |  |  |
| Date Posted |  | 6/15/04 |  |
| Please see the Master List on the ERCOT website for current timeline information. |  |  |  |

| Sponsor |  |
| --- | --- |
| Name | David A. Darnell |
| E-mail Address | dadarnell@cps-ems.com |
| Company | City Public Service |
| Company Address | P.O. Box 1771 , San Antonio, TX, 78296 |
| Phone Number | 210-353-2208 |
| Fax Number |  |

Proposed Operating Guide Language Revision

| Load Shedding and System Restoration | Automatic firm Load shedding will be initiated as follows: Frequency % Load Relief 59.3 Hz 5% 58.9 Hz 10% 58.5 Hz 10% Load shedding will be widely dispersed in each TDSP, with no regard for the REP, and will be accomplished by using high-speed under-frequency relays. Total time from the time frequency is at one of the values specified above (and remains at or below that value) to the time load is interrupted shall be no more than 37 cycles. This includes relay and breaker operation times. If the frequency drops below 58.5 Hz, each TDSP must determine additional steps it will take to survive. Under-frequency relays may be installed on Transmission Facilities under the direction of ERCOT, provided the relays are set at 58.0 cycles or below, are not directional, and have at least 2.0 seconds time delay. Load restoration will be under the direction of the ERCOT Control Area Authority. A TDSP may by mutual agreement, with the approval of the TAC, arrange to have all or part of its automatic Load shedding Obligation carried by another TDSP. ERCOT will be notified and provided with the details of any such arrangement prior to implementation |
| --- | --- |

| ## Other TAC Subcommittee Review |  |
| --- | --- |
| PRS Review Date |  |
| PRS Protocols Impact Decision |  |
| WMS Review Date |  |
| RMS Review Date |  |

| ## TAC Action |  |
| --- | --- |
| TAC Vote Date |  |
| TAC Proposed Implementation Date |  |
| TAC Vote Results |  |

| ## ERCOT Board Action |  |
| --- | --- |
| ERCOT Board Vote Date |  |
| ERCOT Board Implementation Date |  |
| ERCOT Board Results |  |

| ## Appeal |  |
| --- | --- |
| Appeal Date |  |
| Entity Initiating Appeal |  |
| Nature of Appeal |  |