| OGRR Number | 150OGRR | OGRR Title | Clarification to UF Relay Trip Time for Load Shedding |
| --- | --- | --- | --- |
| ###### Date |  | 6/22/04 |  |
| ## Submitter’s Information |  |  |  |
| Name |  | Henry Wood |  |
| E-mail Address |  | hwood@stec.org |  |
| Company |  | STEC/MEC |  |
| Company Address |  | PO Box 119 FM 447 Nursery, TX 77976 |  |
| Phone Number |  | 361-485-6304 |  |

Comments

I would request additional wording changes. These changes should not affect the intent of the OGRR but could assist in further clarification of the guide section.

Revised Proposed Operating Guide Language

| Load Shedding and System Restoration | Automatic firm Load shedding will be initiated as follows: Frequency % Load Relief 59.3 Hz 5% 58.9 Hz 10% 58.5 Hz 10% Load shedding will be widely dispersed in each TDSP, with no preference to REPs, and will be accomplished by using high-speed under-frequency relays. Total time from when frequency is at one of the values specified above (and remains at or below that value) to the time load is interrupted shall be no more than 37 cycles. This includes relay and breaker operation times. If the frequency drops below 58.5 Hz, each TDSP must determine additional steps it will take to avoid system collapse. Under-frequency relays may be installed on Transmission Facilities under the direction of ERCOT, provided the relays are set at 58.0 cycles or below, are not directional, and have at least 2.0 seconds time delay. Load restoration will be under the direction of the ERCOT Control Area Authority. A TDSP may by mutual agreement, with the approval of the TAC, arrange to have all or part of its automatic Load shedding Obligation carried by another TDSP. ERCOT will be notified and provided with the details of any such arrangement prior to implementation |
| --- | --- |