| PRR Number | 425PRR | PRR Title | Section 8 Outage Coordination |
| --- | --- | --- | --- |
| Date |  | September 17, 2003 |  |
| Submitter’s Information |  |  |  |
| Name |  | Steve Myers [Submitted on behalf of Section 8 (PRR 425) Task Force] |  |
| E-mail Address |  | smyers@ercot.com |  |
| Company |  | ERCOT |  |
| Company Address |  | 7620 Metro Center Drive, Austin, TX 78744-1654 |  |
| Phone Number |  | 512/248-3077 |  |
| Fax Number |  |  |  |

Comments

The Section 8 Protocol language revisions shown below represent a complete replacement of Section 8 language in the Protocols.  The language below reflects the combined comments of the PRR 425 Task Force.

Proposed Protocol Language Revision

# Definitions and Acronyms

## Definitions

Outage

Removal of a Facility from service to perform maintenance, construction or repair on the Facility for a specified duration.

Forced Outage (Immediate)

An Outage initiated by protective relay, or manually in response to an observation by personnel or the System Operator that the condition of equipment, an event, or potential event poses a threat to people or equipment. The TSP or Resource may remove such equipment from service immediately and must notify ERCOT of its action immediately.

Maintenance Outage

Removing Transmission Facility or Resource Facility equipment from service to perform work on specific Facility components that could be postponed briefly. Such work is required to prevent a potential Forced Outage and cannot be postponed until the next Planned Outage.  Such Maintenance Outages are classified as follows:

            - Level 1 Maintenance Outage - Equipment that must be removed from service within twenty-four (24) hours to prevent a potential Forced Outage;

            - Level II Maintenance Outage - Equipment that must be removed from service within seven (7) days to prevent a Forced Outage; and,

            - Level III Maintenance Outage - Equipment that must be removed from service within thirty (30) days to prevent a Forced Outage.

Planned Outage

Any major or minor Transmission Facility or Resource Facility equipment maintenance that is planned and scheduled in advance as submitted to ERCOT.

# Outage Coordination

ERCOT’s responsibilities with respect to Outage coordination include:

- Approval of schedules for Planned Outages and Maintenance Outages of Transmission Facilities for Transmission Service Providers (TSPs) in coordination with and based on information regarding all Entities’ Planned Outages and Maintenance Outages;

- Assessment of the adequacy of available Resources relative to forecasts of Load and reserve requirements;

- Coordination and approval of schedules for Planned Outages of Reliability Must Run (RMR) Units subject to the terms of the applicable RMR Agreements;

- Coordination with, and approval of, Outages associated with Black Start Units in accordance with the Black Start Unit Agreement;

- Coordination and approval of changes to existing twelve (12) month Resource Outage plans or proposed Resource Outages requested with eight (8) days Notice or less. Such changes include Resource Outages not previously included in the plan;

- Posting of all proposed and approved schedules for Planned Outages and Maintenance Outages of Transmission Facilities on the ERCOT MIS;

- Creation of aggregated schedules of Planned Outages for Resources and the posting of such schedules on the ERCOT MIS;

- Monitoring of Transmission Facility and Resources Forced Outages and Maintenance Outages of immediate nature and implementing responses to such Outages as provided in these Protocols;

- Establishment and implementation of communication procedures for TSPs to request approval of Transmission Facility Planned Outage and Maintenance Outages schedules;

- Establishment and implementation of record keeping procedures for the retention of all requested Planned Outages, Maintenance Outages, and Forced Outages; and,

- Planning and analysis of Transmission Facility Outages.

## Planned Outages and Maintenance Outages of Transmission and Resource Facilities

### Role of ERCOT

ERCOT will coordinate and approve or disapprove, when applicable, Outages for maintenance, repair, and construction of Transmission and Resources Facilities within the ERCOT System.

Facility owners shall remain solely and directly responsible for the performance of all maintenance, repair, and construction work, whether on energized or de-energized Facilities, including all activities related to providing a safe working environment.

Prior to taking an RMR or a Synchronous Condenser Unit or Black Start Resource (“Reliability Resources”) out of service for a Planned Outage or Maintenance Outage, the Single Point of Contact, as defined in Section 8.2.1, Single Point of Contact, for such RMR Unit, Synchronous Condenser Unit, or Black Start Resource shall obtain ERCOT’s approval of the schedule of the Planned Outage or Maintenance Outage.  ERCOT shall review and approve or reject each proposed Planned Outage or Maintenance Outage schedule as provided in this Section and in accordance with the applicable Agreements.

### Planned Outage or Maintenance Outage Data Reporting

All information submitted in relation to Planned Outages or Maintenance Outages must be submitted by the Resource or the Transmission Service Provider (TSP) in accordance with this section.  Resources and TSPs shall supply to ERCOT the data defined in these Protocols and the Operating Guides.

#### Rolling Twelve Month Outage Planning and Update

#### Transmission Facilities

TSPs must provide ERCOT a written Planned Outage or Maintenance Outage program in an ERCOT provided format for the next twelve (12) months updated monthly for a rolling twelve (12) month period.  Planned Outage or Maintenance Outage scheduling data for Transmission Facilities shall be kept current. Updates must identify all changes to any previously proposed Planned Outages or Maintenance Outage and any additional Planned Outages or Maintenance Outage anticipated over the next twelve (12) months.  ERCOT will coordinate in-depth reviews of the twelve (12) month programs with the TSPs at least two (2) times a year.

#### Resources

Resource Entities must provide ERCOT a written Planned Outage and Maintenance Outage program for the next twelve (12) months, in an ERCOT provided format updated for a rolling twelve (12) month period.  Planned Outage and Maintenance Outage scheduling data for Resource Facilities shall be kept current. Updates shall identify any changes to previously proposed Planned Outages or Maintenance Outages and any additional Planned Outages or Maintenance Outage anticipated over the next twelve (12) months.

If a Resource plans to initiate a Planned or Maintenance Outage within eight (8) days that is not included in the Resource’s written Planned Outage and Maintenance Outage program, such Outage must be approved by ERCOT in advance.  ERCOT will approve or reject requests for such an Outage or changes to an existing Planned Outage program made eight (8) days or less prior to a start date.

ERCOT will assume that Resources not listed as unavailable in the Outage scheduler are available to receive OOM instructions.  ERCOT will discuss reliability issues with the Outage requestor and seek a mutually agreeable resolution prior to rejection.

  - Communications Regarding Resource Facility and Transmission Facility Outages [formerly 8.6]

### Single Point of Contact  [formerly 8.6.1]

All communications concerning Planned Outage or Maintenance Outage shall be between ERCOT and the designated “Single Point of Contact” for each TSP or Resource Entity.  The TSP or Resource Entity shall identify, in its initial request or response, the Single Point of Contact, along with primary and alternate means of communication.  The Resource Entity or Transmission Entity shall submit a Notice of Change of Information (NCI) form when changes occur in a Single Point of Contact.  This identification will be confirmed in all communications with ERCOT regarding proposed or approved Planned Outage or Maintenance Outage requests.

The Single Point of Contact must be either a person or a position available seven (7) days per week and twenty-four (24) hours per day for each Resource Entity and TSP.  The Resource Entity may designate its QSE as its Single Point of Contact.  The Single Point of Contact for the TSP shall be designated in accordance with the ERCOT Operating Guides.

### Method of Communication  [formerly 8.6.2]

Communication between ERCOT and TSPs or Resource Entities shall be accomplished according to ERCOT procedures in compliance with these Protocols.  All submissions, changes, approvals, rejections, and withdrawals regarding Outages shall be processed through the ERCOT Outage Scheduler on the ERCOT MIS, except for Forced Outages and Level I Maintenance Outages, which shall be communicated to ERCOT immediately by voice communication and subsequently entered into the Outage Scheduler.

### Reporting for Planned Outages and Maintenance Outages of  Resource and Transmission Facilities  [formerly 8.1.2.1]

Resource Entities and TSPs shall submit information regarding proposed Planned Outages and Maintenance Outages of Transmission Facilities in accordance with procedures adopted by ERCOT.  The obligation to submit such information applies to Resource Entities and TSPs that have operation and maintenance responsibility for Transmission Facilities and Resources constituting or impacting the ERCOT System.  Resource Entities and TSPs are not obligated to submit information for Transmission Facilities or Resources that are not part of the ERCOT System unless such information is required for regional security coordination as determined by ERCOT.

### Management of Transmission and Resource Forced Outages or Maintenance Outages  [formerly 8.5]

In the event of a Forced Outage, the Resource Entity or TSP may remove the affected equipment from service immediately and must immediately notify ERCOT of its action.  Forced Outages may require ERCOT to review and/or withdraw approval of previously approved Planned Outage or Maintenance Outage schedules to ensure reliability.

For Maintenance Outages, the Resource Entity or TSP shall notify ERCOT of any Resource or Transmission Facility Maintenance Outage according to the Maintenance Outage Levels defined in Section 2, Definitions and Acronyms.  ERCOT will coordinate the removal of facilities from service within the defined timeframes.

ERCOT may require supporting information describing   Forced Outages and Level I Maintenance Outages.  ERCOT may reconsider and withdraw approvals of other previously approved Transmission or Reliability Resource Outages as a result of Forced Outages or Level I Maintenance Outages, if necessary, in ERCOT’s determination to protect system reliability.  When ERCOT approves a Maintenance Outage, ERCOT shall coordinate timing of the appropriate course of action.

Removal of Resource or Transmission Facilities from service under Level 1 Maintenance Outages shall be coordinated with ERCOT.  To minimize harmful impacts to the system in urgent situations, the equipment may be removed immediately from service, provided Notice is given immediately, by the Resource Entity or TSP,  to ERCOT of such action.

### Notification of Forced Outage (Unavoidable Prolongation) of Planned or Maintenance Outage Due to Unforeseen Events

If a Planned or Maintenance Outage is not completed in the ERCOT approved or accepted timeframe, due to weather or unforeseen events, and the Transmission Facilities or Resources are in such a condition that they cannot be restored at the approved completion date, the requesting party shall submit to ERCOT a Forced Outage (Unavoidable Prolongation) form describing the prolongation of the Outage and describing when the equipment will be placed back in service.

## ERCOT Approval of Transmission System Outages [formerly 8.4]

### Approval of Planned Outage and Maintenance Outage of Transmission Facilities [formerly 8.1.2.2]

Proposed Transmission Facility Planned Outage or Maintenance Outage information submitted by a TSP in accordance with this Section constitutes a request for ERCOT’s approval of the Outage schedule associated with the Planned Outage or Maintenance Outage.  ERCOT shall not be deemed to have approved the Outage schedule associated with the Planned Outage or Maintenance Outage until ERCOT notifies the TSP of its approval pursuant to procedures adopted by ERCOT.  ERCOT shall evaluate requests as set forth in Section 8.3.10, Evaluation of Transmission Facility Planned Outage Requests.

[formerly 8.4.1] ERCOT shall approve Planned Outages and Maintenance Outages of Transmission Facilities schedules unless, in ERCOT’s determination, the requested Transmission Facility Planned Outages or Maintenance Outage of Transmission Facilities would cause ERCOT to violate applicable reliability standards.  ERCOT shall transmit its approvals and rejections to TSPs via the ERCOT Outage coordination interface.  Once approved, ERCOT may not withdraw its approval except under the conditions described in Section 8.3.6, Withdrawal of Approval and Rescheduling of Approved Planned Outages and Maintenance Outages of Transmission Facilities.

### Receipt of TSP Requests by ERCOT [formerly 8.4.2 & added text for PIP117]

ERCOT shall acknowledge each request for approval of a Transmission Facility Planned Outage schedule within two (2) Business Hours of the receipt of the request.  ERCOT may request additional information or seek clarification from the TSP regarding the information submitted for a proposed Planned Outage or Maintenance Outage for Transmission Facilities.

    - Timelines for Response by ERCOT  [formerly 8.4.3]

For Transmission Facility Outages, ERCOT shall approve or reject each request in accordance with the following table:

| Amount of time between the request for approval of the proposed Outage and the scheduled start date of the proposed Outage: | ERCOT will approve or reject no later than: |
| --- | --- |
| Three (3) days | 0000 hours, one (1) day prior to start of the proposed Outage |
| Between three (3) and eight (8) days | 0000 hours, two (2) days prior to start of the proposed Outage |
| Between nine (9) days and forty-five (45) days | Four (4) days prior to the start of the proposed Outage |
| Greater than forty-five (45) days | Thirty (30) days prior to the Outage |

ERCOT will make reasonable attempts to accommodate unusual circumstances that support TSP requests for approval earlier than required by the schedule above.

If circumstances prevent adherence to these timetables, ERCOT shall discuss the request status and reason for the delay of the approval with the requesting TSP and make reasonable attempts to mitigate the effect of the delay on the TSP.

When ERCOT rejects a request for an Outage, ERCOT shall provide TSPs, in written or electronic form, suggested amendments to the schedules of Planned Outage or Maintenance Outage of Transmission Facilities. Any such suggested amendments accepted by the TSP shall be processed by ERCOT as a Planned Outage or Maintenance Outage of Transmission Facility request in accordance with this Section.

### Delay  [formerly 8.4.4]

ERCOT may delay its approval or rejection of a proposed Planned Outage or Maintenance Outage of a Transmission Facility schedule if the requesting TSP has not submitted sufficient or complete information within the time frames set forth herein.

### Rejection Notice  [formerly 8.4.5]

If ERCOT rejects a request, ERCOT shall provide the TSP a written or electronic rejection notice that shall include:

- Specific concerns causing the rejection: and,

- Possible remedies or transmission schedule revisions, if any, that might mitigate a basis for approval rejection.

ERCOT may reject Planned Outages or Maintenance Outages of Transmission Facilities only:

- in order to protect system reliability or security; or

- due to insufficient information regarding the Outage; or

- due to failure to comply with approval process requirements

as specified herein.  When multiple proposed Planned Outages or Maintenance Outages cause a reliability or security concern, ERCOT will:

- Communicate with each TSP to see if the TSP will adjust its proposed Planned Outage or Maintenance Outage schedule;

- Determine if the multiple TSPs will agree to an alternative Outage schedule; or

- Reject one or more proposed Outages, considering order of receipt and impact to the ERCOT Transmission Grid, at ERCOT’s discretion.

### Withdrawal of Approval and Rescheduling of Approved Planned Outages and Maintenance Outages of Transmission Facilities   [formerly 8.4.6]

If ERCOT believes it cannot meet the applicable reliability standards and has exercised reasonable options, ERCOT shall have the authority to withdraw approval for a Planned Outage or Maintenance Outage schedule.  ERCOT shall inform the affected TSP both orally and in written or electronic form as soon as ERCOT identifies a situation that may lead to the withdrawal of ERCOT’s approval.  If ERCOT withdraws its approval, the TSP may submit a new request for approval of the Planned Outage or Maintenance Outage schedule.

In determining whether to withdraw approval, ERCOT may give due consideration to whether the Planned Outage or Maintenance Outage affects public infrastructure if ERCOT is made aware of such potential impacts by the TSP (e.g. impacts on highways, ports, municipalities, counties).

### Priority of Approved Planned Outages   [formerly 8.4.7]

In considering TSP requests, ERCOT shall give priority to approved Planned Outage and Maintenance Outage schedules previously posted to the ERCOT MIS.

### Information for Inclusion in Transmission Facility Outage Requests  [formerly 8.1.5]

Transmission Facility Outage requests submitted by TSPs shall include the following Transmission Facility-specific information:

- The identification of the Transmission Facility, including TSP and location;

- The nature of the work to be performed during the proposed Transmission Facility Outage;

- The preferred start and finish date for each proposed Transmission Facility Planned and Maintenance Outage;

- The time required to: (i) terminate the Transmission Facility Planned Outage and Maintenance Outage and (ii) restore the Transmission Facility to normal operation;

- Identification of primary and alternate telephone numbers for the TSP’s Single Point of Contact, as described in Section 8.2.1, Single Point of Contact, and the name of the individual submitting the information;

- The amount of scheduling flexibility (i.e., the earliest start date and the latest finish date for the Outage);

- Identification of any Transmission Facility that must be out of service to facilitate the TSP’s request;

- Identification of any remedial actions or special protection systems necessary during this Outage and the contingency that will require the remedial action or relay action; and,

- Any other  relevant information related to the proposed Outage.

### Additional Information Requests  [formerly 8.1.5.1]

ERCOT may request additional information or seek clarification from the TSP regarding the information submitted for a proposed Outage.

### Evaluation of Transmission Facility Planned Outage or Maintenance Outage Requests  [formerly 8.3]

ERCOT shall evaluate requests for approval of Transmission Facility Planned Outages and Maintenance Outages to determine if any one or a combination of proposed Outages may cause ERCOT to violate applicable reliability standards.  ERCOT’s evaluations shall take into consideration factors including, but not limited to, the following:

- Forecast of peak Demand conditions;

- Outage plans submitted by Resource Entities and TSPs pursuant to Section 8.1, Planned Outages and Maintenance Outages of Transmission and Resource Facilities;

- Forced Outages of Transmission Facilities;

- Potential for the proposed Outages to cause irresolvable transmission overloads or voltage supply concerns based on the indications from contingency analysis software;

- Previously approved Planned Outages and Maintenance Outages;

- Impacts on the transfer capability of DC Ties; and,

- Good Utility Practice with respect to Transmission Facility maintenance.

### Transmission Report  [formerly 8.3.1]

ERCOT will publish on the MIS, initially and when updated, a summary of approved Transmission Facilities Planned Outages, Maintenance Outages, and Forced Outages.

## [new] Approval of Proposed Planned Outages of Resources

Resource Entities must obtain ERCOT approval for all Outage programs or requests made eight (8) or fewer days prior to the proposed Outage start date.

ERCOT will approve these Resource Facility Planned Outage schedules unless, in ERCOT’s determination, the requested Resource Facility Planned Outage would cause ERCOT to violate applicable reliability standards.  ERCOT shall transmit its approvals and rejections to the Resource Entity’s Single Point of Contact via the ERCOT Outage Scheduler.  Once approved, ERCOT may not withdraw its approval except under the conditions described in Section 8.6.2, Withdrawal of Previously Granted Outage Approval(s), except that ERCOT may withdraw such approval if needed, in ERCOT’s determination, to maintain reliability.

### Information for Inclusion in Resources Entity Outage Requests  [formerly 8.1.4]

Resource Entity Outage requests shall include the following information:

- The primary and alternate phone number of the Resource Entity’s Single Point of Contact for Outage coordination.  [new]

- The Resource identified by common name and ESI ID;

- The net megawatts of capacity the Resource Entity anticipates will be available during the Outage (if any);

- The estimated start and finish date for each Planned Outage;

- An estimate of the acceptable deviation in the Outage schedule (i.e., the earliest start date and the latest finish date for the Outage); and,

- The nature of work to be performed during the Outage. [new]

### Additional Information Requests  [formerly 8.1.4.2]

ERCOT may request additional information from a Resource Entity regarding the information submitted as part of a Resource Outage plan.

### Approval of Changes to a Resource Outage Plan within 8 Days of Planned Start [new]

Resource Entities must request approval from ERCOT for new Resource Outages or changes to a Resource Outage plan scheduled to occur within eight (8) days of the request.

ERCOT shall accept Resources Outage changes/submittals unless ERCOT projects that it will be unable to maintain accepted reliability standards if the Outage takes place.  ERCOT will reject a Resource Outage request within this eight (8) day reliability window if it expects this Outage to result in a violation of ERCOT reliability criteria.

ERCOT will accept all changes to a Resource Outage plan submitted by a Resource Entity more than eight (8) days before the planned start date for the Outage.   ERCOT may discuss with Resource Entities or QSEs any Outage requests which are expected to result in a violation of an ERCOT reliability criteria or which may result in cancellation of a planned transmission Outage in an attempt to reach a mutually agreeable resolution, including rescheduling the Outage in a manner agreeable to the Resource.

Notwithstanding the conditions stated above, any Resource may return from a Planned Outage when the scheduled work is complete without ERCOT approval.  In the event of such an early return the Resource or QSE will notify ERCOT of the early return as much in advance as practicable, but no later than at least two (2) hours prior to startup.

### Timelines for Response by ERCOT [new]

ERCOT shall approve or reject each request in accordance with the following table:

| Amount of time between a Request for approval of a proposed Outage and the scheduled start of the proposed Outage: | ERCOT will approve or reject no later than: |
| --- | --- |
| Between one (1) and two (2) days | Within eight (8) Business Hours of receipt by ERCOT |
| Between three (3) and eight (8) days | 0000 hours, two (2) days prior to start of the proposed Outage |
| Greater than eight (8) Days | Accepted, but ERCOT may discuss reliability and scheduling impacts to minimize hazard/cost to ERCOT System in an attempt to accomplish minimum overall impact. |

### Delay [new]

ERCOT may delay its approval or rejection of a proposed Planned Outage schedule if the requesting Resource Entity has not submitted sufficient or complete information within the time frames set forth in this Section.  Review periods for Outage consideration shall not commence until sufficient and complete information is submitted to ERCOT.

### Opportunity Outage

Opportunity Outages are a special category of Planned Outages that may be approved by ERCOT when a specific Resource has been forced off line due to a Forced Outage and the Resource has been previously approved or accepted for a Planned Outage within the next eight (8) days.

When a forced Outage occurs on a Resource that has an approved or accepted Outage scheduled within the following eight (8) days, the Resource may remain off line and start the accepted/approved Outage earlier than scheduled, provided ERCOT is provided as much advance notice as practicable, but no later than two (2) hours prior to startup.

### Outage Returning Early[new]

A Resource that completes a scheduled Outage early may resume operation without ERCOT approval; however, the Resource’s QSE shall notify ERCOT of the early return prior to resuming service.  In the event of such an early return, the Resource or QSE must notify ERCOT of the early return as much in advance as practicable, but no later than at least two (2) hours prior to startup.  If ERCOT cannot maintain a secure state with this Resource injection, the Resource may be issued a Dispatch Instruction to OOM offline to restore a secure state.

Prior to an early return from an Outage, a Resource or QSE may inquire of ERCOT if the Resource is expected to be issued a Dispatch Instruction to provide OOM service to zero upon its early return.  Notwithstanding any other provisions of these Protocols, if a Resource/QSE makes this inquiry, is notified by ERCOT that it will OOM the unit offline if it returns from the Outage early, and still starts within the previously approved/accepted Outage period, then the QSE host to this Resource will not be paid startup and OOM energy compensation as otherwise would be provided for in these Protocols.

## Approval of RMR Unit, Synchronous Condenser Unit or Black Start Resource Outages [new]

ERCOT shall evaluate requests for approval of RMR Unit, Synchronous Condenser Unit, and Black Start Resource (Reliability Resources) Outages to determine if any one or a combination of proposed Outages may cause ERCOT to violate applicable reliability standards. ERCOT’s evaluations shall take into consideration factors including, but not limited to, the following:

- Load Forecast;

- All other known Outages; and,

- Potential for the proposed Outages to cause irresolvable transmission overloads or voltage supply concerns based on the indications from contingency analysis software.

ERCOT shall approve requests for Planned Outages of Reliability Resources unless, in ERCOT’s determination, the requested Outage would cause ERCOT to violate applicable reliability standards.  ERCOT shall approve or reject each request in accordance with the following table:

### Timelines for Response by ERCOT on Reliability Resource Outages[new]

| Amount of time between a Request for approval of a proposed Planned Outage and the scheduled start date of the proposed Outage: | ERCOT will approve or reject no later than: |
| --- | --- |
| No less than thirty (30) days | Fifteen (15) days prior to start of the proposed Outage |
| Greater than forty-five (45) days | Thirty (30) days prior to the start of the proposed Outage |

ERCOT shall approve requests for Outages, other than Forced Outages or Level I Maintenance Outages, of  Reliability Resources unless, in ERCOT’s determination, the requested Outage would cause ERCOT to violate applicable reliability standards.  ERCOT will approve or reject uMaintenance Outages on Reliability Resources as follows:

Clarification

| Amount of time between a Request for approval of a proposed Maintenance Outage | ERCOT will approve or reject no later than: |
| --- | --- |
| Between three (3) and eight (8) days | 0000 hours, two (2) days prior to start of the proposed Outage |
| Between nine (9) and thirty (30) Days | Four (4) days prior to the start of the proposed Outage |

ERCOT shall not be deemed to have approved the Outage request associated with the Planned Outage until ERCOT notifies the Single Point of Contact of its approval. ERCOT will transmit approvals electronically.

### Changes to an Approved Reliability Resource Outage Plan [new]

Once ERCOT has approved a Reliability Resource Planned Outage, a Market Participant may submit to ERCOT a change request form (in addition to entering the change in the Outage Scheduler) no later than thirty (30) days before the scheduled start date of the approved Outage.  ERCOT will accept or reject the proposed change within fifteen (15) days of receiving the change request form. ERCOT may, at its discretion, relax the thirty (30) day notice requirement.

## Management of Resource Outages [new]

### Rejection of Proposed Resource Outages [new]

This Section 8.6.1, Rejection of Proposed Resource Outages, applies to changes to existing Outage schedules submitted eight (8) days or less prior to the Outage start date, to new Outage requests submitted eight (8) days or less prior to the proposed start date for the Outage, and to Reliability Resource Outages.

If a proposed Resource Outage, in conjunction with previously approved Outages, would cause a violation of applicable reliability standards, ERCOT will reject the Outage approval and notify the relevant Single Point of Contact for the Resource requesting the Outage.  Provided, however, ERCOT will consider other reasonable means to avoid the violation of applicable reliability standards prior to issuing such Outage disapproval.

When a proposed Resource Planned Outage and/or a Transmission Facility Outage cause reliability or security concerns, ERCOT will:

(1)	Communicate with each requesting Market Participant to try to identify how to adjust the proposed Outage requests; and,

(2)	Reject one or more proposed Transmission or Reliability Resource Outage(s), considering order of receipt and impact to the ERCOT System, at ERCOT’s discretion.  If security cannot be maintained after these actions, then rejection of Resource Outages in order of receipt or impact will be considered.

ERCOT will normally reject proposed Outages when its analysis indicates an Outage will result in the insecurity or unreliability of the ERCOT System.  Based upon security and reliability analysis results, ERCOT shall investigate possible Remedial Action Plans for all insecure states and strive to maximize transmission usage consistent with reliable operation.  ERCOT will reject Outage requests if it cannot identify Remedial Action Plans for any security concerns relating to an Outage.

### Withdrawal of Previously Granted Outage Approval(s) [new]

If ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options, ERCOT shall withdraw approval for Transmission or Reliability Resource Outage(s) as necessary.  ERCOT shall inform the Single Point of Contact for the affected Market Participant, both orally and in written or electronic form, as soon as ERCOT identifies a situation that may lead to the withdrawal of ERCOT’s approval.  If ERCOT withdraws its approval, the Resource Entity may submit a new request for approval of the Outage.

If ERCOT cannot meet applicable reliability standardsERCOT will discuss the reliability problem with the Single Point Of Contact representing other Resources where Outages are negatively affecting system reliability to reach mutually agreeable solutions, which may include changes to Outage schedules that are agreeable to the facility Entities.

### Deratings [new]

The Resource Entity or its designee must enter deratings extending more than twenty-four (24) hours in the ERCOT Outage Scheduler.

## Analysis of Resource Adequacy [formerly 8.2]

### Calculation of Aggregate Generating Capacity [formerly 8.2.1]

ERCOT shall use Planned Outages submitted by Resource Entities pursuant to Section 8.1, Planned Outages and Maintenance Outages of Transmission and Resource Facilities, to calculate the aggregate capacity from Resources projected to be available in each Congestion Zone.  On a rolling twelve (12) month basis, ERCOT shall calculate the aggregate weekly Resource capacity by Congestion Zone projected to be available during the peak Load hours of each week of the following twelve (12) months.

### System Adequacy Report  [formerly 8.2.2]

On a rolling twelve (12) month basis, ERCOT shall analyze system adequacy for the ERCOT System and each Congestion Zone, comparing the minimum aggregated weekly peak Resource capacity to the weekly peak forecast Demand for the next twelve (12) months.

ERCOT shall report projected peak Resource capacity deficiencies to Market Participants.  ERCOT shall update this report monthly using the latest Resource Planned Outages.  ERCOT shall post the report on the MIS.  The information published in the report shall be limited to a notice of deficiency, if any, projected to occur in each Congestion Zone during each week of the rolling twelve (12) month period.

### Long-Term-Demand Forecasts [formerly 8.2.3]

ERCOT shall develop and publish monthly on the MIS peak Demand forecasts for each week of the next twelve (12) months.  During the development of this forecast, ERCOT may consult with QSEs, TDSPs and other Market Participants that may have knowledge of potential Load growth.

ERCOT may, at its discretion, publish on the MIS additional peak Demand analyses for periods beyond twelve (12) months.

## For Transmission Facility Outages, ERCOT shall approve or reject each request in accordance with the following table:

  - Coordination for System Topology Modifications [formerly 8.7]

### Coordination with ERCOT  [formerly 8.7.1]

Prior to energizing and placing into service any new or relocated Facility connected to the ERCOT Transmission Grid, TSPs shall coordinate with and receive approval from ERCOT.

### Types of Work Requiring Coordination  [formerly 8.7.2]

TSPs shall coordinate with ERCOT the following types of work for any addition, replacement or modification to the ERCOT Transmission Grid:

- Transmission lines forming part of the ERCOT Transmission Grid;

- Equipment including circuit breakers, transformers, disconnects, reactive devices, and wave traps forming part of the Transmission Facility;

- Resource interconnections; and,

- Protection and control schemes, including Remedial Action Plan (RAP), Supervisory Control And Data Acquisition, Energy Management System, AGC, or Special Protection Schemes (SPS).

#### TSP Information to be Provided to ERCOT  [formerly 8.7.2.1]

The TSP shall notify ERCOT at least thirty (30) days before starting to energize or place into service any new or relocated Facility.  The notice shall include:

(1)	TSP performing work;

(2)	Location Code if applicable;

(3)	Identification of existing Transmission Facilities involved and new Transmission Facilities (if any) being added or existing Transmission Facilities being permanently removed from service;

(4)	Outages required (clearly identify each Outage if multiple Outages are required), including sequence of Outage and estimate of Outage duration;

(5)	General statement of work to be completed with intermediate progress dates and events identified;

(6)	Supervisory Control and Data Acquisition modification work;

(7)	Complete descriptions of any new data telemetry points or changes to existing telemetry;

(8)	Procedure for reporting work accomplished, including reporting to ERCOT, TSP and the QSE representing the Resources involved;

(9)	General description of the method to be used to energize and test new/rebuilt Transmission Facilities;

(10)	In service testing, including:

  - Procedure to be performed; and,

  - Notice of testing completion.

(11)	Statement of completion, including:

  - Statement to be made at the completion of each section of program; and,

  - Statement to be made at completion of total project.

(12)	Drawings to be attached, including:

  - Existing status;

  - For each intermediate stage; and,

  - Proposed completion of job.

#### Approval of the Work  [formerly 8.7.2.2]

On receipt of the information set forth in Section 8.8.2.1, TSP Information to be Provided to ERCOT, ERCOT shall review the information and notify the TSP or Resource of any required modifications.  ERCOT may, at its discretion, require changes to and more detail regarding the work for the procedure.  The requesting TSP or Resource will consult with other Entities likely to be affected and will revise the work plan, following any necessary or appropriate discussions with ERCOT and other affected Entities.  ERCOT shall approve or reject the request, including any revisions made by the TSP, within fifteen (15) days of receipt of the complete request and any revisions.  Following ERCOT approval, where appropriate, ERCOT shall publish a summary of the approved work on the MIS.

#### Changes to Work Approved by ERCOT  [formerly 8.7.2.3]

The TSP shall notify ERCOT and any other affected TSPs as soon as practicable of any requested changes to the work plan.  ERCOT shall review and approve or reject changes to the work in accordance with Section 8.8, Coordination for System Topology Modifications.

#### Approval of Work Requiring Coordination  [formerly 8.7.2.4]

ERCOT shall maintain a record of all work approved in accordance with Section 8.8, Coordination for System Topology Modifications, and shall publish information on the MIS regarding each new Transmission Facility to be installed on the ERCOT transmission grid.