| PRR Number | 493PRR | PRR Title | Induction Generator Exemption |
| --- | --- | --- | --- |
| Protocol Section(s) Requiring Revision (include Section No. and Title) |  | 6.5.7.1(7) Generation Resources Required to Provide VSS Installed Reactive Capability |  |
| Requested Resolution (Normal or Urgent) |  | URGENT – Note that I am only requesting urgent status; because there was an indication that this was the desired timetable by the TAC. Absent this indication from TAC, I could not justify urgent status on my own. Please don’t ask me to justify it. |  |
| Revision Description |  | Revise section to clarify the mechanism an induction generator may use to receive an exemption from the generator and the level of the payment to be made. |  |
| Reason for Revision |  | See revision description. |  |
| Timeline |  |  |  |
| Date Posted |  | 2/12/04 |  |
| Please see the Master List on the ERCOT website for current timeline information. |  |  |  |

| Sponsor |  |
| --- | --- |
| Name | Richard Ross |
| E-mail Address | rross@aep.com |
| Company | AEP |
| Company Address | 2 West 2nd Street Tulsa, OK 74137 |
| Phone Number | 918-594-2906 |
| Fax Number | 866-947-1796 |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

|  | Impact |  | Benefit |
| --- | --- | --- | --- |
|  | Business | Computer Systems |  |
| ERCOT | None | None | Clarifies procedure for receiving and the cost of exemption for induction generators. |
| MARKET SEGMENT | None | None | None |
| Consumer | None | None | Assures that the cost of installing equipment to replace the Reactive Power not being provided by the induction generator is comparable to the cost being paid for the exemption, so that exemptions are neutral with respect to Transmission Cost of Service. Lays the foundation that this cost is subject to change in the future as construction costs and/or technology changes. |
| LSE: General, Including NOIE | None | None | Same as consumer. |
| LSE: CR & REP | None | None | Same as consumer. |
| QSE | None | None | None |
| Resource | None | None | Same as ERCOT. |
| TDSP | None | None | Same as consumer. |

Comments

Note that the $52,150 figure is based on a combination of Static/Shunt Capacitor and Dynamic reactive devices the TDSP would have to install to provide the necessary steady state and transient reactive requirements.  Individually the costs of these types of devices are $32,000/MVAR and $125,000/MVAR (transient basis; $250,000/MVAR steady state) basis respectively.  For each MW of installed capability these types of devices contribute $10,000/MW and $42,150/MW respectively to the total cost of $52,150/MW reflected in the PRR language.

There may be options available to induction generators to fulfill this requirement that are less costly than $52,150/MW.  The objective of this language should not be to provide them a lower cost alternative, but rather provide a figure representative of the cost the TDSP will incur if the induction generator chooses, through this exemption, have the TDSP satisfy the obligation.

Proposed Protocol Language Revision

## {The baseline language shown below is taken from PRR473 (Reactive Standards), which is scheduled for the February 17 Board of Directors meeting.  The baseline language shown below will be implemented March 1, 2004 if approved.}

## 6.5	Technical Requirements for Providers of Ancillary Services

6.5.7	Voltage Support Service

6.5.7.1	Generation Resources Required to Provide VSS Installed Reactive Capability

- Generation Resources required to provide VSS must be capable of producing a defined quantity of Reactive Power at rated capability (MW) to maintain a Voltage Profile established by ERCOT.  This quantity of Reactive Power is the Unit Reactive Limit (URL).

- Generation Resources required to provide VSS whose installations were in operation on September 1, 1999 or later, except as noted below, shall have and maintain a URL which has an over-excited (lagging) power factor capability, of ninety-five hundredths (0.95) or less and an under-excited (leading) power factor capability of ninety-five hundredths (0.95) or less, both determined at the generating unit's maximum net power to be supplied to the transmission grid and at the transmission system Voltage Profile established by ERCOT, and both measured at the point of interconnection to the TDSP.

- Qualified renewable Generation Resources (as described in Section 14, Renewable Energy Credit Trading Program) in operation before [INSERT ERCOT BOARD APPROVAL DATE] required to provide VSS and all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999 whose current design does not allow them to meet the URL as stated above, will be required to maintain a URL that is limited to the quantity of Reactive Power that the Generation Resource can produce at it’s rated capability (MW) as determined using procedures and criteria described in the Operating Guides.

- New generating units connected before [INSERT ERCOT BOARD APPROVAL DATE + 15 MONTHS] whose owners demonstrate to ERCOT’s satisfaction that design and/or equipment procurement decisions were made prior to [INSERT ERCOT BOARD APPROVAL DATE], based upon previous standards, whose design does not allow them to meet the URL as stated above, will be required to maintain a URL that is limited to the quantity of Reactive Power that the Generation Resource can produce at its rated capability (MW) as determined using procedures and criteria described in the Operating Guides.

- Upon request to, and with the approval of ERCOT, multiple generating units connected to the same transmission bus may be treated as a single generating unit for the purposes of these URL requirements only.

- Upon submission by a Generation Resource required to provide VSS to ERCOT of a specific proposal for requirements to substitute for these URL requirements, ERCOT shall either approve such alternative requirements or provide the submitter an explanation of its objections to the proposal.  Alternative requirements may include supplying additional static and/or dynamic Reactive Power capability as necessary to meet the area’s Reactive Power requirements.

- An induction generator may elect to make a contribution in aide of construction in lieu of meeting the installed capacity requirements contained herein as provided in this Section 6.5.7.1 (7).  In order to receive such an exemption the generator must make a payment to the interconnecting TDSP under its generation Interconnection Agreement in a manner similar to that used to collect payments for the direct assignment of interconnection Facilities under PUCT Substantive Rules 25.195(c)(1) and 25.198(d)(1).  The level of payment, which may be revised at any time to reflect the changes in cost of construction of reactive equipment, will be fifty-two thousand one hundred fifty dollars ($52,150) per rated MW for the generator.  This level of payment and exemption is contingent upon the generator making sufficient substation space available and accessible for use by the TDSP for the installation of the reactive equipment that is required to replace the reactive capability that otherwise would have been provided by the generator.  Such payments will be reflected in the interconnecting TDSPs rates as provide for under the applicable PUCT Substantive Rules.

- For Generation Resources required to provide VSS, no unit equipment replacement or modification shall reduce the capability of the unit below the requirements to be met by that unit prior to the replacement/modification, unless specifically approved by ERCOT.

- Generation Resources required to provide VSS shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT (conveyed by way of their QSE) unless equipment damage is imminent.