ERCOT ISO PROTOCOL
METERING ATTACHMENT

Technical Metering Attachment Index

Technical Metering Attachment a:	FAILURE OF ISO FACILITIES

Technical Metering Attachment b:	CERTIFICATION PROCESS FOR METERING FACILITIES

Technical Metering Attachment c:	METER CONFIGURATION CRITERIA

Technical Metering Attachment D:	STANDARDS FOR METERING FACILITIES

Technical Metering Attachment e:	TRANSFORMER AND LINE LOSS CORRECTION FACTORS

Technical Metering Attachment F:	INSTRUMENT TRANSFORMER RATIO AND CABLE LOSS CORRECTION FACTORS

Technical Metering Attachment G:	ISO DATA VALIDATION, ESTIMATION AND EDITING PROCEDURES

Technical Metering Attachment H:	Settlement Data Overview Concept

Technical Metering Attachment a:	FAILURE OF ISo FACILITIES

- Primary ISO Communication Link Unavailable

  - Unavailable Functions of Primary ISO Communication Link

During a total disruption of the Primary ISO Communication Link the ISO may not be able to:

##### communicate with ERCOT Polled Settlement Meters or TDSPs to acquire or provide any Meter Data or Settlement Quality Meter Data;  or

##### communicate general information.

  - Communications during Primary ISO Communication Link Unavailability

During any period of Primary ISO Communication Link unavailability, the ISO shall:

##### make all reasonable efforts to provide general information to TDSPs using voice communications; and

##### inform TDSPs of the methods they must use to provide Meter Data and Settlement Quality Meter Data to the ISO during that period.

- Primary MDS Master Station Completely Unavailable

  - Notification of Loss of Primary MDS Master Station

In the event that the primary MDS master station becomes completely unavailable, the ISO will use alternate communications to notify the redundant MDS master station that the primary MDS master station is unavailable.

  - Notification of Restoration of Primary MDS Master Station

The ISO will post confirmation on the ISO Web Site that all computer systems are functioning normally (if such be the case) and use the redundant MDS master station to take complete control of the all MDS functions.  Once the primary MDS master station is again available, all functions will be transferred back to the primary MDS master station and the ISO will notify all TDSPs via the  ISO Web Site or other appropriate communication method.

Technical Metering Attachment b:	CERTIFICATION Form FOR METERING FACILITIES

The form below is to be used in the certification process described in the ERCOT ISO Protocols Section 10.

| ISO Meter Certification Form |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Facility Information |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Name: |  |  |  |  |  |  |  |  |  | Unit Name: |  |  |  |  |  |  |  |  |  |  |
| Address: |  |  |  |  |  |  |  |  |  | Drawing Numbers: (see note 1) |  |  |  |  |  |  |  |  |  |  |
| TDSP Contact : |  |  |  |  |  |  |  |  |  | Phone Number: |  |  |  |  |  |  |  |  |  |  |
| Scheduled ISO Inspection Date: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Generator Information |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Gross Output |  |  |  |  |  |  |  |  |  | Auxiliary Load |  |  |  |  |  |  |  |  |  |  |
| Net Output |  |  |  |  |  |  |  |  |  | Voltage / Connections |  |  |  |  |  |  |  |  |  |  |
| Revenue Billing Information |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Meter Manufacturer |  |  |  |  |  |  |  |  |  | Register Constant |  |  |  |  |  |  |  |  |  |  |
| Meter Serial Number |  |  |  |  |  |  |  |  |  | Program ID Number |  |  |  |  |  |  |  |  |  |  |
| Meter Type |  |  |  |  |  |  |  |  |  | Device ID |  |  |  |  |  |  |  |  |  |  |
| Meter Form |  |  |  |  |  |  |  |  |  | IP Address/Router Port # |  |  |  |  |  |  |  |  |  |  |
| Does meter have external pulse inputs for totalization purposes? Yes  (info. is attached) No  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Internal Mass Memory Constants |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Function |  |  | Channel |  |  |  | Ke |  | PRI KWH Constant |  |  |  | Interval Size |  |  |  |  |  | Display Sequence |  |
| KWH DELIVERED |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| KVARH DEL |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| KVARH REC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| KWH RECEIVED |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Voltage Transformer Information |  |  |  |  |  |  |  |  |  |  | Current Transformer Information |  |  |  |  |  |  |  |  |  |
| Name Plate |  |  |  | A |  | B |  | C |  |  | Name Plate |  |  | A |  |  |  | B |  | C |
| Manufacturer |  |  |  |  |  |  |  |  |  |  | Manufacturer |  |  |  |  |  |  |  |  |  |
| Serial Number |  |  |  |  |  |  |  |  |  |  | Serial Number |  |  |  |  |  |  |  |  |  |
| Type |  |  |  |  |  |  |  |  |  |  | Type |  |  |  |  |  |  |  |  |  |
| Ratio |  |  |  |  |  |  |  |  |  |  | Ratio |  |  |  |  |  |  |  |  |  |
| Voltage Class |  |  |  |  |  |  |  |  |  |  | Voltage Class |  |  |  |  |  |  |  |  |  |
| BIL Rating |  |  |  |  |  |  |  |  |  |  | BIL Rating |  |  |  |  |  |  |  |  |  |
| Accuracy Class |  |  |  |  |  |  |  |  |  |  | Accuracy Class |  |  |  |  |  |  |  |  |  |
| Burden Rating |  |  |  |  |  |  |  |  |  |  | Rating Factor |  |  |  |  |  |  |  |  |  |
| Connected Burden |  |  |  |  |  |  |  |  |  |  | Burden Rating |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Connected Burden |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Applied Test Burden |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Burden Test |  |  | Pass Fail  |  |  |  | Pass Fail  |  | Pass Fail  |
| Instrument Transformer Correction Factors (FCF) (see note 2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Full Load |  |  |  |  |  |  | Power Factor |  |  |  |  |  |  |  | Light Load |  |  |  |  |  |
| Transformer Loss Compensation Values (at Full Load Meter Rating) (see note 2 and 3) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| % Watt Fe Loss |  |  |  |  |  |  |  |  |  | % Var Fe Loss |  |  |  |  |  |  |  |  |  |  |
| % Watt Cu Loss |  |  |  |  |  |  |  |  |  | % Var Cu Loss |  |  |  |  |  |  |  |  |  |  |
| Total Compensation Values (at Full Load Meter Rating) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| % Watt Total Loss |  |  |  |  |  |  |  |  |  | % Var Total Loss |  |  |  |  |  |  |  |  |  |  |
| Completed by: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Date: |  |  |  |
| Remarks: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Reviewed by: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Date: |  |  |  |

Notes:

- TDSPs shall provide a copy of the one line diagram and schematics detailing the connections from the instrument transformer to the meter, communication circuit and local meter data server (if applicable)in accordance with this Technical Metering Attachment for all ERCOT Polled Settlement Meters they own.

- TDSPs shall attach a copy of the calculations used to determine these values.

- For Power Transformer Loss Correction and Radial Line Loss Correction values the appropriate sign (+/-) should be utilized depending on the flow of Energy (delivered/received) and the location of the Interconnection Meter Point.

Technical Metering Attachment c:	EPS METER CONFIGURATION CRITERIA

- Power Flow Conventions

Meters shall be installed and configured in such a manner so as to define the 4 Quadrants referred to in Exhibit 1 to Technical Metering Attachment D of this Protocol.

- EPS Meter Standard Memory Channel Assignments

For metering with bi-directional power flows, ERCOT will require metering which will measure 4 quadrant Vars.  Therefore, six channels of data will be required. Such Metering Facilities shall be installed and configured in such a manner so as to comply with the following ERCOT requirements:

- Channel 1 shall record active power delivered by the ERCOT Transmission System;

- Channel 2 shall record quadrant 1 reactive power delivered by the ERCOT Transmission System;

- Channel 3 shall record quadrant 3 reactive power received by the ERCOT Transmission System;

- Channel 4 shall record active power received by the ERCOT Transmission System;

- Channel 5 shall record quadrant 2 reactive power delivered by the ERCOT Transmission System; and

- Channel 6 shall record quadrant 4 reactive power received by the ERCOT Transmission System.

- Standard Meter Display Modes

The following display readings shall be displayed in the normal display mode to comply with ERCOT requirements.

Normal Display Mode (Optional Configuration, Bi-directional Kwh and Four Quadrant kVarh)

For metering bi-directional power flows in which the ISO requires 4 quadrant Var measurement, the following items should be displayed in the sequence listed below:

- Segment check.

- Date MM:DD:YY.

- Time HH:MM:SS (Central Standard time adjusted for DST, military format).

- Total kWh delivered by the ERCOT Transmission System.

- Maximum kWd  (15 minute demand interval) delivered by the ERCOT Transmission System.

- Date and time of maximum kWd delivered by the ERCOT Transmission System.

- Total kVarh for Quadrant 1.

- Total kVarh for Quadrant 2.

- Total kVarh for Quadrant 3.

- Total kVarh for Quadrant 4.

- Total kWh received by the ERCOT Transmission System.

- Maximum kWd (5 minute or hourly demand interval) received by the ERCOT Transmission System.

- Date and time of maximum kWd received by the ERCOT Transmission System.

Consumption Values

The consumption values shall be in XXXXX.X format and demand in XXXX.XX format.  The register scaling factor should be set such that the display does not roll over in less than 60 days.

Alternative Display Mode

The values listed below should be displayed in the alternate display mode to comply with ISO requirements:

- Phase A voltage magnitude and phase angle.

- Phase B voltage magnitude and phase angle.

- Phase C voltage magnitude and phase angle.

- Phase A current magnitude and phase angle.

- Phase B current magnitude and phase angle.

- Phase C current magnitude and phase angle.

- Neutral current magnitude and phase angle (if available).

- Instantaneous kW delivered by the ERCOT Transmission System (for bi-directional power flows and/or applications where the power flow is out of ERCOT Transmission System).

- Instantaneous kW received by the ERCOT Transmission System (for bi-directional power flows and/or applications where the power flow is received by the ERCOT Transmission System).

When available, the alternative display mode may also be used on EPS meters to display other definable quantities in sequence after the values defined above.

- Test Mode Display

The following values should be displayed in the test mode to comply with ISO requirements:

- total pulse count for test; and

- total consumption during test.

During the test mode the above values should be provided for each function being tested (Watts, Vars). The data displayed by the meter while in test mode shall not change the normal mode display registers nor shall it be recorded in the load profile channels. This requirement is imposed to prevent the test data from being recorded as actual load/generation data.

Additional display quantities may be added in sequence in the test mode after the values defined above by the TDSP.

- Transformer and Line Loss Correction

The TDSP will be responsible for properly calculating and applying the transformer and line loss corrections to its EPS Meters in accordance with Section 10 of the Protocol and this Attachment to reflect the actual meter usage (on the low side) as opposed to the theoretical meter usage at the transmission point.

- CT/VT and Cable Loss Correction Factors

Where the connected burden of a metering circuit exceeds the burden rating of a CT or VT or if an existing instrument transformer does not meet the minimum ISO accuracy requirements, then one of the actions listed below must to be taken:

- replace the instrument transformer(s) with higher burden rated revenue class units; or

- reduce the burden on the circuit to comply with the name plate of existing instrument transformer(s); or

- Special Applications, Configurations and Unique Situations

TDSPs are responsible for providing the ISO with the necessary EPS Meter Data and other information to enable the ISO to prepare Settlement Quality Meter Data.

For instance, where there is a generating plant with multiple generators and auxiliary loads, the TDSP must provide appropriate information (i.e. documentation, descriptions, one line diagrams, etc.) to the ISO to ensure that the ISO can properly account for the net generator output of each unit under all combinations of generation and load (e.g. where only one generator is operating but all auxiliary loads are being supplied).

Technical Metering Attachment D:	STANDARDS FOR METERING FACILITIES

The standards for Metering Facilities referred to in this Technical Meter Attachment provide additional details to the standards referred to in Section 10 of the ERCOT ISO Protocols Document.

The standards referred to in the Protocol, and this Technical Meter Attachment apply to all meters used in ERCOT for settlement purposes as well as real time metering used by the ISO for validation of ancillary services.  At this time the attachment includes standards for ERCOT Polled Settlement (EPS) Meters and IDR type meters.  Other levels of metering will be added later prior to metering becoming competitive.

- Standards for Existing Metering Facilities

Existing Metering Facilities are those facilities that are fully installed as of the Market Operations Date.  Existing Metering Facilities used as EPS metersshall meet the following general standards:

- revenue quality instrument transformers  must have an accuracy class of 0.3% or better

- revenue metering must have an accuracy class of .2% or better once the transition period has ended

- netted generator auxiliary load metering must meet all revenue settlement accuracy standards applicable to the installation

- General Standards for New Generation Meters

New Meters are those meters that are installed after the Market Operations Date.  New Meters used  as EPS Meters shall meet the following general standards:

- they must be revenue quality in a 0.2% accuracy class of ANSI C12.20 and applicable ERCOT Guides.

- they must be remotely accessible, 60 Hz, three phase, bi-directional, programmable and multifunction electronic meters

- they must be capable of being remotely time synchronized by ERCOT (MV90).

- they must be capable of measuring kWh and kVarh and providing calculated three phase values for kVah, kVa

- there must be battery back-up for maintaining RAM and a real-time clock during outages of up to thirty days

- there must be AC potential indicators on each of the three phases

- they must be capable of being powered either internally from the bus or externally from a standard 120 volt AC source.

- they must be capable of providing (MV-90) addressable metering protocol

- they must be capable of 30 days storage of kWh and KVarh interval data

If there is any inconsistency between these general standards and the detailed standards referred to in paragraphs D3 and D4 of this Technical Metering Attachment, the detailed standards shall prevail.

- General Standards for New Zonal UFE Meters (process is being developed but should be similar to the IDR standard)

- they must be revenue quality in a .2% accuracy class of ANSI C12.20 and applicable ERCOT Guides.

- they must be remotely accessible, 60 Hz, three phase, bi-directional, programmable and multifunction electronic meters

- they must be capable of measuring kWh and kVarh

- there must be battery back-up for maintaining RAM and a real-time clock during outages of up to thirty days

- there must be AC potential indicators on each of the three phases

- they must be capable of being powered either internally from the bus or externally from a standard 120 volt AC source.

- they must be capable of providing (MV-90) addressable metering protocol

- they must be capable of 30 days storage of kWh and KVarh interval data

If there is any inconsistency between these general standards and the detailed standards referred to in paragraphs D3 and D4 of this Technical Metering Attachment, the detailed standards shall prevail.

- Detailed Standards for New Meters

Exhibit 1 to this Technical Meter Attachment provides the detailed specifications with which new meters must comply.

- Detailed Standards for New Instrument Transformers

Exhibit 2 to this Technical Meter Attachment provides the detailed specifications with which new instrument transformers must comply.

EXHIBIT 1 TO technical Meter attachment D

ENGINEERING SPECIFICATION

FOR POLYPHASE SOLID-STATE

ELECTRICITY REVENUE QUALITY METERS

FOR USE ON THE ERCOT TRANSMISSION SYSTEM

TABLE OF CONTENTS

1	General Information

2	Scope

2.1	General

2.2	Applicability

3	Metering Functions

3.1	Measured Quantities

3.2	Basic Default Metering Function

3.3	Demand Metering Function

3.4	Load Profile Function

3.5	Function during Power Disturbances

3.6	Meter Test Mode Function

4	Display Requirements

4.1	Display

4.2	Display Components

4.3	Digits

4.4	Time Format

4.5	Date Format

4.6	Operating Modes

4.7	Normal Mode

4.8	Alternate Mode

4.9	Display Items

4.10	Identifiers

5	Meter Diagnostics

5.1	Self-test

5.2	Diagnostic Checks

5.3	Pulse Overrun

5.4	Error and Warning Displays

5.5	Error Reset

6	Programming and Software

6.1	Local Communications Interface.

6.2	Meter Programmers

6.3	Software

6.4	Communication Protocol

7	Communication

7.1	Optical Port

7.2	Baud Rate

7.3	Optical Port Location

7.4	Optical Port Cable

7.5	RS232 or RS 485 or RSXXX.

8	Optional Meter Functions

9	Accuracy

9.1	ANSI C12.10, .2% Accuracy Class

9.2	Test Equipment

9.3	Creep

9.4	Start Up Delay

10	Electrical Requirements

10.1	Meter Forms, Voltage Ratings and Classes

10.2	Metering Application

10.3	Connections

10.4	Meter Register Power Supply

10.5	Clock

10.6	Batteries

10.7	Electromagnetic Compatibility

10.8	Radio Interference Suppression

11	Mechanical Requirements

11.1	General

11.2	Corrosion Protection

11.3	Solar Radiation

11.4	Corrosive Atmospheres

11.5	Meter Package

11.6	Nameplate

12	Security

12.1	Billing Period Reset

12.2	Meter Password

12.3	Revenue Protection

13	Meter Approval Testing

13.1	General Requirement

13.2	Meter Failure Definition

13.3	Accuracy Test

13.4	Line Voltage Variation Test

13.5	Momentary Power Loss

13.6	Power Failure Backup System Test

13.7	Effect of Temperature Variation on Clock Accuracy

13.8	Temperature Cycle Test

13.9	Humidity Cycle Test

13.10	Insulation Withstand Test

13.11	Standard Waveform Surge Withstand Test

13.12	Fast Transient Waveform Surge Withstand Test

13.13	Powerline Surge Voltage and Current Test

13.14	Electrostatic Susceptibility Test

13.15	Shipping Test

14	Safety

15	Data Security And Performance

16	HARDWARE DOCUMENTATION TO BE PROVIDED FOR ISO REVIEW

17	Applicable Standards

18	Definitions

- General Information

This Exhibit applies to all solid-state polyphase electricity meters used in revenue metering applications using ERCOT Polled Settlement (EPS)Meters.

- Scope

  - General

This Exhibit provides the minimum functional and performance requirements for Meters.  All requirements in this Exhibit are intended to ensure the expected life cycles, security, accuracy, reliability and minimum maintenance requirement of Meters.  Some requirements, however, are specified to maintain the compatibility and interchangeability of the Meter.

  - Applicability

Meters approved under this Exhibit may not be required to have all of the specified features.  Meters shall meet the specified minimum requirements and the requirements of Section 13 (Meter Approval Testing) of this Exhibit.

- Metering Functions

  - Measured Quantities

As used in this Exhibit, the term “delivered” applies to Energy flowing out of the ERCOT Transmission System and the term “received” applies to Energy flowing into the ERCOT Transmission System.

    - Consumption

The following consumption quantities are required for all Meters approved for use on the ERCOT Transmission System:

      - Kilowatt-hours—delivered;

      - Kilowatt-hours—received;

      - Kilovar-hours—for each quadrant;

    - Demand

The following demand quantities are required for all meters approved for use on the ERCOT Transmission System:

      - Kilowatts—delivered;

      - Kilowatts—received;

      - Kilovars—for each quadrant; and

    - Power Factors

All transmission connected loads will be required to maintain a .95 power factor.  The meter for these loads will need to be capable of properly recording power factor or loading to develop a power factor from calculations to meet the Protocol requirements established. Reverse Consumption/Demand

The Meter shall be programmable to take one of the following actions for reverse consumption and demand quantities:

      - ignore the reverse quantities; and

      - add the reverse quantities to the appropriate consumption and demand quantities.

  - Basic Default Metering Function

Once the meter is programmed and tested to meet the ERCOT requirements, the meter should not require a battery to maintain its program.  An unprogrammed meter shall indicate on its display that it is not programmed.

  - Demand Metering Function

Meters shall have the following demand metering functions:

      - as a minimum, the Meter shall be programmable for fixed and/or rolling interval demand calculations on bi-directional kilowatts and kilovars;

      - a battery shall not be required to perform demand calculations, to save the results or to communicate the results to a handheld meter reader connected to the optical port;

      - the Meter shall be programmable for one minute delivered kilowatt demand (as an approximation of “instantaneous” kilowatts delivered) in addition to the rolling interval demand calculation.  The one minute demand is not required to be synchronous with the other demand quantities;

      - the Meter shall be programmable for rolling interval demand calculations for any optional demand quantity (see Section 3.1.2) that the ISO specifies.

      - demand intervals shall be programmable for a duration of 5, 10, 15, 30 or 60 minutes;

      - the demand interval shall be composed of an integral number of sub-intervals.  Sub-interval duration shall be a programmable duration of 1, 5, 10, 15 or 30 minutes;

      - demand functions shall be capable of temporary suspension for a programmable time interval after power is restored following a power outage.  The length of time shall be programmable from zero to 60 minutes in one minute intervals;

      - after a demand reset, further manual demand resets shall be prevented with a programmable lockout time.  A demand reset from a Meter Programmer connected to the optical port is not subject to this delay and can be initiated as frequently as required; and

  - Data Recording Function

Meters shall have the following data recording functions:

      - ERCOT may specify that the Meter provide load profile recording of interval data for 6 channels of consumption quantities;

      - date and time shall be stored with the load recording of interval data;

      - load recording of interval data shall use a “wraparound” memory that stores new interval data by writing over the oldest interval data;

      - the load recording of interval data function shall be capable of storing and communicating a minimum of 60 days of 6 channel, 15 minute interval data, in addition to allowances for event recording (power outages, resets, time sets, etc.);

      - the load recording of interval data function shall have the capacity to count and store at least 4,000 counts in a 15 minute period of time; and

      - load recording of interval data shall continue while the Meter is communicating with a Meter Programmer connected to the optical port.

  - Function during Power Disturbances

Meters shall have the following functions during power disturbances:

      - during powerline disturbances such as brownout or outage conditions the Meter shall maintain all meter data as well as time keeping functions.  Display and communication functions are not required during these conditions;

      - the Meter shall withstand the following outages during a continuous ten year or longer service without the need to maintain its auxiliary power system, including replacing the battery:

            - 20 short outages per year of less than 30 seconds per outage; and

            - 40 days of continuous/cumulative outage;

      - during a power outage, critical program and billing data shall be written to non-volatile memory.  When power is restored, data shall be returned to active memory and data collection resumed;

      - following a power outage, register “catch-up” time shall be a maximum of 30 seconds.  During the “catch-up” time the Meter shall still calculate consumption and demand quantities.  Optional outputs shall also function during this time;

      - during power outages, time shall be maintained with a cumulative error of no more than 2 minutes per week (0.02%);

      - the Meter shall record the date and time of any power outage; and may also record the duration of any power outage.

  - Meter Test Mode Function

Meters shall have the following meter test mode functions:

      - the Meter shall have the capability of a Test Mode function that suspends normal metering operation during testing so that additional consumption and demand from the tests are not added to the Meter’s totals;

      - the Test Mode function shall be activated by a permanently mounted physical device that requires removal of the Meter cover to access or by a Meter Programmer connected to the communications port;

      - activation of the Test Mode shall cause all present critical billing data to be stored in non-volatile memory and restored at the time of exit from the Test Mode;

      - upon activation of the Test Mode, register displays shall accumulate beginning from zero;

      - actuation of the billing period reset device during Test Mode shall reset the test mode registers;

      - after a programmable time-out period, the Meter will automatically exit from Test Mode and return to normal metering; and

      - the default Test Mode registers for an unprogrammed meter shall include as a minimum:

            - time remaining in the test interval;

            - maximum kilowatt block demand; and

            - total kilowatt-hours.

- Display Requirements

  - Display

The Meter shall have an electronic display for displaying the consumption and demand quantities in accordance with ANSI C12.20.

  - Display Components

The display shall provide the following:

      - six digits for display of the consumption and demand quantities and constants with programmable decimal point location for the three least significant digits;

      - three digits for numeric display identifiers (ID numbers);

      - alternate and Test Mode indication;

      - potential indication for each phase;

      - end of interval indicator;

      - visual representation of the magnitude and direction of kilowatt loading;

      - visual representation of the magnitude and direction of kilovar loading; and

      - Annunciators for consumption and demand quantities.

  - Digits

Consumption and demand quantities shall be programmable for display with leading zeroes in four, five or six digits with a decimal point at any of the least significant three digits.

  - Time Format

Time shall be displayed in the 24 hour military format Central Standard Time adjusted for daylight savings time in the appropriate periods in the meter.

  - Date Format

Date shall be displayed programmable in Month/Day/Year format.

  - Operating Modes

The display shall have the following operating modes:

      - Normal Mode – in this mode, the display shall scroll automatically through the programmed displays for normal meter reading;

      - Alternate Mode – in this mode, the display shall scroll automatically, scroll manually or freeze for up to one minute for alternate programmed displays; and

      - Test Mode – in this mode, the display shall scroll automatically, scroll manually or freeze for up to one minute for test quantity displays.

Display ID numbers, and sequence shall be independently programmable for each of the modes referred to above.  Display times shall be programmable.

  - Normal Mode

Upon power-up, the Meter display shall operate in the Normal Mode.  The Meter display shall operate in Normal Mode until power is disconnected or until either the Alternate Mode or the Test Mode is activated.

  - Alternate Mode

The Alternate Mode shall be initiated with a display control device that does not require Meter cover removal or with a Meter Programmer connected to a communications port.

Display Items

As a minimum, the Meter shall provide the display quantities and items for each of the modes referred to in Section 4.6 as detailed in Attachment 2.

  - Constants and Correction Factors.

The Meter shall be programmable to account for radial line losses and power transformer loss correction.

The meter shall be programmable to display the corrected values.  The values will be programmable in kWh, kVARh, etc.  Decimal places shall be programmed to appropriately display the value.

(DO WE NEED TO STANDARDIZE THE DISPLAY OF kWh/kVARh OR SHOULD THIS BE OPTIONAL?)

  - Identifiers

The Meter shall have programmable identifiers for the Meter ID, the person who programmed the Meter (programmer ID) and the current program ID.  The Meter ID shall be capable of eight alphanumeric characters.

- Meter Diagnostics

  - Self-test

The Meter register shall be capable of performing a self-test of the register software.  As a minimum, the self-test shall be performed at the following times:

      - whenever communications are established to the register;

      - after a power-up; and

      - once per day.

  - Diagnostic Checks

As a minimum, the following diagnostic checks shall be performed during a self-test:

      - check the backup battery usage or voltage;

      - verify the program integrity; and

      - verify the memory integrity.

  - Pulse Overrun

The register shall be capable of detecting that the maximum number of pulses have been exceeded during a demand interval.

  - Error and Warning Displays

Meters shall be capable of the following displays:

      - any detected error or warning shall be stored in memory and an error or warning code displayed on the display;

      - error code displays shall freeze the display; and

      - warning code displays shall be programmable to one of the following choices:

            - freeze the warning code on the display;

            - ignore the warning code (not displayed); or

            - warning code display at the end of the Normal, Alternate or Test Modes display sequences.

  - Error Reset

Error or warning conditions shall only be reset upon an explicit command invoked via the Meter Programmer or upon some other explicit action by the Meter technician.

- Programming and Software

  - Local Communications Interface.

The Meter shall be capable of communicating with a handheld reader or personal computer through a local port.

  - Meter Programmers

The TDSP and ERCOT Authorized Inspectors will use PC DOS/Window based laptop or handheld computers as meter programming devices.  Communications with the Meter shall be through the meter’s local or remote port.

  - Software

The TDSP shall ensure that its meter supplier provides all software for maintenance, programming and operation of the Meter.

  - Communication Protocol

The protocol used for communication with the Meter through the optical port, local comm. port or the modem shall be an asynchronous, byte oriented protocol.

Optical port communications shall meet ANSI C12.18, communications with comm. ports shall meet ANSI C12.22 (when finalized) and modem communications shall meet ANSI C12.21.

- Communication

  - Optical Port

The communication port to the Meter for reading and programming of the internal data shall be an optically isolated communication port per ANSI C12.18, Type 2 or other serial port.

  - Baud Rate

The optical port shall communicate at a minimum of 9600 baud.

  - Optical Port Location

The optical port shall be located in the front of the Meter and be accessible without removing the Meter’s cover.

  - Internal/External Modem

Internal or external modems shall be capable of telephone communications at autobaud rates at a minimum of 1,200 baud.  The modem shall include automatic baud select, configurable answer time window and configurable answer ringcounter.  The ring detect circuitry shall not be affected by spurious voltage rises in the telephone line.

  - RS232 or RS 485 or RSXXX.

One RSXXX port shall be provided at the Meter for bi-directional communications (with security provisions included) to computers and/or data acquisition devices.  The Meter must have the capability for being polled every 15 minutes for data by the ERCOT Meter Data Acquisition System or a Compatible Meter Data Server.  An optional RSXXX port or ports with read-only access can be provided for others desiring the data.  All RSXXX ports shall be optically isolated.

The Meter shall be capable of being polled simultaneously by more than one entity(locally and remotely, or by multiple remote ports) without loss of data, interference, lockup or other such problems.  In all cases, priority servicing shall be given to the ISO required RSXXX port (used by MDAS).  If multiple modems are present, the primary modem shall be used for ERCOT communications.

- Optional Meter Functions

The ISO may specify additional metering options as they require.

- Accuracy

  - ANSI C12.20, 0.2 Accuracy Class

The Meter shall meet or exceed the accuracy specifications contained in ANSI C12.20, 0.2 Accuracy Class, over its entire service life without the need for adjustment.

  - Test Equipment

Meter accuracy and calibration tests, both shop and field, shall require only standard test equipment.  No special laboratory-type test equipment or test procedures shall be required to assure accuracy of the Meter.

  - Creep

The Meter shall not creep.  No pulse generation or registration shall occur for any consumption or demand quantity which depends on current while the current circuit is open.  An exception to this is made for meters programmed for line and transformer loss compensation, where pulse generation and registration shall not exceed the amount required for such compensation.

  - Start-up Delay

The Meter shall start to calculate consumption and demand quantities less than 3 seconds after power application.

- Electrical Requirements

  - Meter Forms, Voltage Ratings and Classes

The following forms, voltage ratings and classes of Meters are approved for installation on the ERCOT Transmission System:

      - A – Base Type, 120 Volts, Class 10 and Class 20;

      - Socket – Type, 120 Volts, Class 10 and Class 20;

- Forms shall comply with ANSI C12.10 (excluding 2½ element meters).

      - Switchboard – Type, 2 Element (generation only) and 3 Element, 120 Volts, Class 10 & Class 20; and

      - Rack mounted meter assemblies – 2 element and 3 element, Class 10 & Class 20.

      - ISO approved Class 2 meters can be used where optically isolated CTs are used.

  - Metering Application

The Meter shall be used to meter electrical service on a continuous duty.

  - Connections

The Meter’s internal electrical connections shall be in accordance with ANSI C12.10.

  - Meter Register Power Supply

The Meter register shall be powered from the line side of the Meter and shall have provision for external backup power.

  - Clock

Clocks shall meet the following requirements:

      - the clock internal to the Meter shall be accurate within 2 minutes per week (0.02%) when not synchronized to the ERCOT Transmission System operation line frequency and shall be resettable through the ISO communications interface.

      - Should the internal clock, when polled, be found to be outside the ERCOT designated window for time accuracy, the meter’s internal clock will be synchronized by ERCOT through the MV90 system;

      - the internal clock shall have two modes of operation as follows:

            - the clock shall synchronize with the ERCOT Transmission System operation line frequency until an outage occurs.  During the outage, the clock will then synchronize with its own internal crystal.  When power returns, the clock shall resynchronize with the ISO’s master synchronizing signal and follow line frequency; and

            - the clock shall always synchronize with its own internal crystal, as a default; and

      - the choice of clock mode shall be programmable.

  - Batteries

Batteries shall meet the following requirements:

      - when the Meter design requires a battery as auxiliary power supply, the requirements of Section 3.5 shall apply;

      - the battery shall be secured with a holder securely attached to the Meter.  The battery holder and electrical connections shall be designed to prevent the battery from being installed with reversed polarity;

      - replaceable batteries shall be easily accessible by removing the Meter cover.  Battery replacement while the Meter is in service shall not interfere with any of the specified functions;

      - no fuse external to the battery shall be installed in the battery circuit;

      - the Meter battery shall provide a minimum carryover capability at 23° C for the functions listed in Section 3.5 and have a 15 year shelf life; and

      - the following information shall be clearly identified on the battery:

            - manufacturer;

            - date of manufacture, including year and month (i.e. 0001) or year and week (i.e. 0044);

            - polarity;

            - voltage rating; and

            - type.

  - Electromagnetic Compatibility

The Meter shall be designed in such a way that conducted or radiated electromagnetic disturbances as well as electrostatic discharges do not damage nor substantially influence the Meter.

  - Radio Interference Suppression

The Meter shall:

      - not generate conducted or radiated radio frequency noise which could interfere with other equipment; and

      - meet FCC Part 15 Class B computing device radio frequency interference standards.

- Mechanical Requirements

  - General

The Meter shall not pose any danger when operating under rated conditions in its normal working position.  Particular attention should be paid to the following:

      - personnel protection against electric shock;

      - personnel protection against effects of excessive temperature;

      - protection against the spread of fire; and

      - protection against penetration of solid objects, dust or water.

  - Corrosion Protection

All parts of the Meter shall be effectively protected against corrosion under normal operating conditions.  Protective coatings shall not be damaged by ordinary handling nor damaged due to exposure to air.  The Meter shall be capable of operating in atmospheres of up to (and including) 95% relative humidity condensing.

  - Solar Radiation

The functions of the Meter shall not be impaired, the appearance of the Meter shall not be altered and the legibility of the Meter nameplate and other labels shall not be reduced due to exposure to solar radiation throughout the service life of the Meter.

  - Corrosive Atmospheres

ERCOT may specify additional requirements for Meters used in corrosive atmospheres.

  - Meter Package

The Meter Package shall meet the following requirements where applicable:

      - the socket and “A” base Meter’s dimensions shall be in accordance with ANSI C12.10;

      - Panelboard meters shall be in accordance with applicableNEC standards;

      - the socket and “A” base Meter shall be designed for mounting outdoors;

      - Panelboard meters must be mounted indoors or in an enclosure that meets all applicable NEMA standards.

      - Meters shall have a cover capable of being sealed in accordance with ANSI C12.10 requirements.  The Meter cover shall:

            - be resistant to ultraviolet radiation if used outdoors;

            - be sealed in such a way that the internal parts of the Meter are accessible only after breaking the seal(s);

            - for any non-permanent cover deformation, not prevent the satisfactory operation of the meter;

            - for the “sprue” hole (mold fill hole), not affect the ability to read the Meter; and

- have capability of being interrogated at the meter via an optical port per ANSI C12.18, Type 2 or digital communications port.

      - the method of securing the socket Meter to the meter socket shall be with either a sealing ring or a high security sealing device;

      - the billing period demand reset device shall accommodate a standard electric meter seal and shall remain in place with friction if not sealed; and

      - filtered ventilation shall be provided in the base of the Meter to prevent condensation inside the Meter.

  - Nameplate

The Meter nameplate shall comply with the minimum information requirements of ANSI C12.10;

- Security

  - Billing Period Reset

Operation of the billing period demand reset mechanism shall require breaking of a mechanical sealing device.  Use of common utility-type sealing devices shall be accommodated.

  - Meter Password

The Meter shall be programmable by the Meter Programmer with a minimum of two unique passwords to prevent unauthorized tampering by use of the optical port or the optional modem.  For meters procured after 1/1/01, passwords must be a minimum of four (4) alpha/numeric characters.  Access rights and capabilities shall be individually programmable for each password.  The Meter shall accept multiple requests from different sources without error, lockup or loss of data.

  - Revenue Protection

Meters that help prevent Energy diversion are preferred.

- Meter Approval Testing

  - General Requirement

This Section outlines the testing required by the ISO to assure the quality of Meters, the ISO will not approve Meters which have not undergone the testing referred to in this Section.

All meters shall be in compliance with ANSI C12.20 at the 0.2 Accuracy Class and ANSI C12.1 with the exception of metering used with optically isolated CT’s (class 2 metering).  Class 2 meters shall meet the same standards listed in this attachment as applicable.

ISO Testing using Independent Laboratory

In addition to the required manufacturer testing specified in this Section, the ISO reserves the right to require independent laboratory test data resulting from the performance of tests as outlined in this Section.

In addition to the applicable testing requirements of the ANSI C12 standards, the qualification tests specified in this Section shall be conducted to confirm correct operation of the Meter.

The qualification testing is required for new Meter designs.

ERCOT will determine whether this same testing is required for Meter product changes that may affect their compliance with this Attachment.

The TDSP shall ensure that its EPS Meter supplier provides a certified test report documenting the tests and their results.  The test report will be signed by the supplier and shall include all charts, graphs and data recorded during testing.

  - Meter Failure Definition

A Meter shall be designated as failed if any of the following events occur:

      - failure of the Meter to perform all of the specified functions;

      - failure of the Meter to meet the technical performance specifications included in this Exhibit;

      - signs of physical damage or performance degradation as a result of a test procedure, including effects which could shorten the service life of the Meter;

      - the occurrence of an unexpected change of state, loss of data or other unacceptable mode of operation for the Meter as a consequence of a test procedure; and

      - failures shall be classified as a hardware, firmware or software failure or a combination according to the following definitions:

            - firmware failures are errors made during the fabrication of programmable read only memory (PROM) chips such that the required program or instruction set that the microprocessor is to perform is incorrect;

            - hardware failures are failures that are physical in nature and directly traceable to the component level.  Visual observances such as discoloration, cracking, hardening of cables, poor solder joints, etc. are also included.  Failures of DIP switches, jumpers, and links are also included; and

            - software failures are failures such as the loss or unintended change of data, the inability to program the Meter, the loss of the Meter program or the erroneous output or display of false information.

  - Accuracy Test

This test confirms the accuracy of the Meter:

      - the accuracy of the Meter shall be tested for all combinations of conditions as defined by ANSI C12.20 .2% accuracy class.

      - accuracy curves from these tests shall be provided to the ERCOT ISO.

  - Line Voltage Variation Test

This test confirms the Meter’s correct operation under varying line voltage conditions and shall be performed per ANSI C12.20, 0.2 accuracy class.

  - Momentary Power Loss

This test confirms the Meter’s ability to withstand momentary power outages and shall be performed per ANSI C12.20, 0.2 accuracy class.

  - Power Failure Backup System Test

This test confirms the carryover capability of the Power Failure Backup System and shall be performed per ANSI C12.20, 0.2 accuracy class.

  - Effect of Temperature Variation on Clock Accuracy

This test confirms the effects of temperature on the Meter clock accuracy and shall be performed per ANSI C12.20, 0.2 accuracy class.

  - Temperature Cycle Test

This test confirms the effects of an accelerated temperature cycle on the Meter and shall be performed per ANSI C12.20, 0.2 accuracy class.

  - Humidity Cycle Test

This test confirms the effects of an accelerated humidity cycle on the Meter and shall be performed per ANSI C12.20, 0.2 accuracy class.

  - Insulation Withstand Test

This test confirms the insulation levels of the Meter and shall be performed per ANSI C12.20, 0.2 accuracy class.

  - Standard Waveform Surge Withstand Test

This test confirms the ability of the Meter to withstand voltage transients and shall be performed per ANSI C12.20, 0.2 accuracy class.

  - Fast Transient Waveform Surge Withstand Test

This test confirms the ability of the Meter to withstand fast voltage transients and shall be performed per ANSI C12.20, 0.2 accuracy class.

  - Powerline Surge Voltage and Current Test

This test confirms the ability of the Meter to withstand power line voltage and current surges and shall be performed per ANSI C12.1.

  - Electrostatic Susceptibility Test

This test verifies the ability of the Meter to withstand electrostatic discharges and shall be performed per ANSI C12.20, 0.2 accuracy class.

  - Shipping Test

This test confirms the ability of the Meter and its packaging to withstand the rigors of shipping and handling and shall be performed per ANSI C12.20 tests 29, 30, 31, and 32, 0.2 accuracy class.

- Safety

  - Hazardous Voltage

Hazardous voltages shall not be easily accessible with the Meter cover removed.

  - Grounding

All accessible conductive parts on the exterior of the Meter and conductive parts that are accessible upon removal of the Meter cover shall be electrically connected to the Meter grounding tabs.  All connections in the grounding circuit shall be made with an effective bonding technique.

  - Toxic Materials

No materials that are toxic to life or harmful to the environment shall be exposed in the Meter during normal use.

  - Fire Hazard

Materials used in the construction of the Meter shall not create a fire hazard.

- Data Security And Performance

      - No loss of data shall occur as a result of the following events within design specifications:

            - power outages, frequency changes, transients, harmonics, reprogramming, reading; and

            - environmental factors—dampness, heat, cold, vibration, dust.

      - 15 minute interval data for the most recent 60 day period shall always be available and accessible via the communications interface or the optical interface.

- Hardware Documentation To Be Provided for ISO Review

      - Drawing(s) showing the external meter connections.

      - Instruction booklets detailing the necessary procedures and precautions for installation of the Meter provided for use by field personnel during initial installation written in the style of a step by step outline.

      - One (1) technical/maintenance manual and one (1) repair manual shall be provided for each Meter style.  These manuals shall be sufficiently detailed so that circuit operation can be understood and equipment repair facilitated.

      - The above documents shall be submitted for approval by ERCOT before equipment is installed.  Approval of documents by ERCOT shall not relieve any responsibility for complying with all the requirements of this Exhibit.

- Definitions

The following terms and expressions used in this Exhibit are detailed as set forth below:

“Ambient Temperature” means temperature of 23°±2° Celsius.

“Average Power Factor” means the power factor calculated using the average active and reactive power flows over the latest demand interval.

“Delivered” means Energy (active, reactive, or apparent) that flows from the ERCOT Transmission System to an End-User.

“Failed Meter” means a Meter in which any part or component, except the removable battery, has failed.

“Failure” means any hardware, firmware or software failure, or any combination.

“Hazardous Voltage” means any voltage exceeding 30 volts rms.

“Meter” means all single phase and three phase electricity meters with electronic registers, including hybrid and solid state meters, but excluding solid state recorders, and including any optional devices included under the Meter cover.

“Meter Programmer” means the laptop computers used for meter reading/programming.

“MSDS” means the Material Safety Data Sheet.

“Power Failure Backup System” means a sub-system in the Meter that provides power to the electronic circuitry when the normal power line voltage is below operating limits.  The sub-system usually consists of a battery and may or may not include a super capacitor.

“Quadrant” means the term used to represent the direction of power flows (active and reactive) between the ERCOT Transmission System and an End-User.  The 4 quadrants are defined as follows:

      - Quadrant 1 – shall measure active power and reactive power delivered by the ERCOT Transmission System;

      - Quadrant 2 – shall measure active power received by ERCOT Transmission System and reactive power delivered by the ERCOT Transmission System;

      - Quadrant 3 – shall measure active power and reactive power received by the ERCOT Transmission System; and

      - Quadrant 4 – shall measure active power delivered by ERCOT Transmission System and reactive power received by the ERCOT Transmission System.

“Received” means Energy (active, reactive or apparent) that flows from a Generator to the ERCOT Transmission System.

“RFI” means the Radio Frequency Interference.

“TDSP” means Transmission/Distribution Service Provider.

“Temperature tolerance” means ±2° Celsius.

Attachment 1

Physical and Electronic Attribute Criterion for Electricity Meters

| Test / Inspection Description | Pass | Fail |
| --- | --- | --- |
| 1. Bayonets |  |  |
| A. Missing or loose parts, i.e., cotter pin, arc gap, etc. |  |  |
| 2. Meter Base |  |  |
| A. Any cracked and/or missing/damaged gasket |  |  |
| B. Any broken leg |  |  |
| C. Missing or loose voltage link or screw |  |  |
| D. Any missing or loose arc gaps |  |  |
| E. Missing or damaged ventilation screen or filter on applicable meter |  |  |
| F. Sealing hole unusable for sealing |  |  |
| G. Any chips on upper half of meter (gasket ring area) |  |  |
| H. Any chips which may jeopardize meter integrity |  |  |
| I. Any sign of water damage in meter such as corrosion, oxidation, stain |  |  |
| J. Missing or loose rivets holding frame to base |  |  |
| 3. Meter Frame |  |  |
| A. Nameplate data incorrect or flawed |  |  |
| B. Missing or loose hardware on frame |  |  |
| 4. Module |  |  |
| A. Loose or defective power connectors |  |  |
| B. Improper routing of voltage leads |  |  |
| C. Improper fit (loose or crooked) |  |  |
| D. Crimped or pinched voltage leads |  |  |
| E. Incorrect module |  |  |
| F. Calibration screw access should not be significantly affected (or covered) |  |  |
| 5. Meter Cover |  |  |
| A. Wiring to communication port is correct & solid |  |  |
| B. Proper meter cover is used for meter type and class |  |  |
| C. Mechanical reset mechanism works properly |  |  |
| D. Proper alignment, positioning, and operation of all cover mechanisms |  |  |
| 6. Electronic Register |  |  |
| A. Program register to verify acceptance of rate schedule |  |  |
| B. Check display that all segments are operational |  |  |
| C. Check battery carryover function, if appropriate |  |  |
| D. Check register tracking by inputting disk revolutions |  |  |
| E. Check for any visual defects in the register assembly |  |  |

Only scratches and/or chips that are cosmetically or functionally objectionable will be classified as defective and failing.

| Attachment 2 Meter Display Items |  |  |  |  |
| --- | --- | --- | --- | --- |
| Display Item | Normal Mode | Alternate Mode | Test Mode |  |
| Minimum Requirements for Delivered kWh |  |  |  |  |
| Complete Display (Segment) Test | x | x |  |  |
| Demand Reset Count |  | x |  |  |
| Demand Reset Date |  | x |  |  |
| Instantaneous kW | x | x |  |  |
| Interval length |  | x |  |  |
| Minutes of Battery Use |  | x |  |  |
| Present time | x | x |  |  |
| A phase voltage & phase angle |  | x |  |  |
| B phase voltage & phase angle |  | x |  |  |
| C phase voltage & phase angle |  | x |  |  |
| A phase current & phase angle |  | x |  |  |
| B phase current & phase angle |  | x |  |  |
| C phase current & phase angle |  | X |  |  |
| Neutral current & phase angle (if available) |  | x |  |  |
| Program ID |  | X |  |  |

| Attachment 2 Meter Display Items (cont.) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Display Item | Normal Mode |  | Alternate Mode |  | Test Mode |  |
| Minimum Requirements for Delivered kWh (cont.) |  |  |  |  |  |  |
| Total kWh Delivered | x |  | X |  | x |  |
| Wh per disk revolution (Kh) |  |  | X |  |  |  |
| Wh per pulse (Ke) |  |  | X |  |  |  |
| Wh per test output indication (Kt) |  |  | X |  | x |  |
| Total kWh Received | X |  | x |  |  |  |
| Minimum Requirements for Test Mode |  |  |  |  |  |  |
| Present Interval Demand—kW |  |  |  |  | X |  |
| Pulse count |  |  |  |  | X |  |
| Time left in subinterval |  |  |  |  | X |  |
| Total kWh |  |  |  |  | X |  |
| Maximum kW demand Delivered | X |  |  |  |  |  |
| Maximum kW Demand Received | X |  |  |  |  |  |
| Date and time of Max. Demand Delivered | X |  |  |  |  |  |
| Date and time of Max. Demand Received | X |  |  |  |  |  |
| Additional requirements for kVARh (if specified) |  |  |  |  |  |  |
| kVARh Quadrant 1 | X |  |  |  |  |  |
| kVARh Quadrant 2 | X |  |  |  |  |  |
| kVARh Quadrant 3 | X |  |  |  |  |  |
| kVARh Quadrant 4 | X |  |  |  |  |  |
| Additional requirements for kVAh (if specified) |  |  |  |  |  |  |
| Attachment 2 Meter Display Items (cont.) |  |  |  |  |  |  |
| Display Item | Normal Mode | Alternate Mode |  | Test Mode |  |  |
| Additional requirements for Power Factor (if specified) |  |  |  |  |  |  |
| Quadrant 1 Average Power Factor |  | X |  |  |  |  |
| Quadrant 2 Average Power Factor |  | X |  |  |  |  |
| Quadrant 3 Average Power Factor |  | X |  |  |  |  |
| Quadrant 4 Average Power Factor |  | X |  |  |  |  |
| Instantaneous Power Factor |  | X |  |  |  |  |
| Total Average Power Factor Delivered |  | X |  |  |  |  |
| Total Average Power Factor Received |  | X |  |  |  |  |

EXHIBIT 2 TO Technical Meter Attachment D

ISO SPECIFICATION
FOR CERTIFICATION of INSTRUMENT TRANSFORMERS 
FOR REVENUE METERING

- Purpose

This Exhibit specifies the technical requirements for high-accuracy Current Transformers (CT), and Voltage Transformers (VT) to be used for settlement metering on the ERCOT Transmission System.

- Scope

  - This Exhibit applies to the following:

- Oil-filled Single-Phase CTs.

- Oil-filled Single-Phase VTs.

- Oil-filled Single-Phase Combination Current/Voltage Transformers.

- Coupling Capacitor Voltage Transformers.

- Fiber Optic CTs.

- Standards

All instrument transformers covered by this Exhibit shall be designed, manufactured, tested and supplied in accordance with the applicable national standards and as required by the ERCOT Protocols and this Metering Attachment.

- Definitions

“Hermetically Sealed” means completely sealed by fusion, soldering, etc., so as to keep air or gas from getting in or out (i.e. airtight).

“Metering Unit” means one or more Voltage element(s) and one or more Current element(s) contained in one common housing.

“BIL Rating” means basic lightning impulse insulation level.

“Burden Rating” means the total impedance (in ohms) that can be connected to the secondary circuit(s) of an instrument transformer while still maintaining metering accuracy of plus-or-minus 0.3%

- Specifications

  - General

All instrument transformers covered by this Exhibit shall have a minimum BIL Rating appropriate for the designated nominal System voltage:

- Up to 15 kV – 110 kV BIL

- 25kV – 150 kV BIL

- 35kV – 150 kV

- 60 - 69 kV – 350 kV BIL

- 138 kV – 650 kV BIL

- 345 kV – 1300 kV BIL

  - Current Transformers

Current Transformers shall be either wire wound CTs or a fiber optic system which includes:  the physical unit, the optical sensor, the fiber optic cable, and optical conversion electronics.

    - Current Transformer windings (typical configurations) shall be either:

        - a single primary winding and single secondary winding with dual ratio tap;

        - a dual primary winding and a single ratio tap;

        - a single primary winding and one or more secondary windings with dual ratio tap(s); or

        - other combinations as available and approved by the ERCOT.

    - Rated primary current

The rating selected for primary current must be as specified by the TDSP based on supplied information.

    - Rated secondary current (Wire Wound)

The rated secondary current must be 5 amperes @ rated primary current.

    - Rated output (Fiber Optic System)

The output of the electronics in the fiber optic control unit shall be converted to 1 ampere @ rated primary current and used with an ANSI class 2 style meter.

    - Accuracy and burden (Wire Wound)

All current transformers shall have an accuracy and burden of:

        - standard – plus-or-minus 0.3% @ B0.1 - 1.8 ohms, 10% - 100% rated current; or

        - optional – plus-or-minus 0.15 % @ B0.1 - 1.8 ohms, 5% - 100 % rated current.

    - Accuracy and burden (Fiber Optic System)

All fiber optic CT metering systems shall have an accuracy and burden of:

        - standard – plus-or-minus 0.3%, ensuring that fiber connection is maintained within manufacturer’s prescribed limits. (This recognizes that optical units have an accuracy range closer to 0.15% from 5% to nominal current rating.)

    - Continuous current rating factor

All current transformers shall meet or exceed a continuous current rating factor of:

        - standard – 1.5 @ 30 degrees C Ambient; or

        - optional – 1.0 @ 30 degrees C Ambient.

    - Short time thermal current rating

The short time thermal current rating varies with transformer rating as follows:

25/50: 5 ratio, 4 kA RMS to 1500/3000:5 ratio, 120 kA RMS.

    - Mechanical short time current rating

The mechanical short time current rating varies with transformer rating as follows:

25/50:5 ratio, 3 kA RMS to 1500/3000:5 ratio, 90 kA RMS.

  - Voltage Transformers

    - Transformer windings shall consist of a single primary winding and one or more tapped secondary windings.

    - Rated primary voltage, will be specified by the TDSP.

    - Rated secondary voltage will typically be 115/69 volts.

    - Accuracy and burden

All voltage transformers shall have accuracy and burden of:

        - standard – plus-or-minus 0.3% through B.  ZZ @ 90% through 110% of nominal voltage; or

        - optional – plus-or-minus 0.15% through B.  Y 90% through 110% of nominal voltage.

    - Thermal burden rating

All voltage transformers shall have a thermal burden rating of:

        - 34.5 kV – 2500 VA, 60 hertz;

        - 60 kV & 69 kV – 4000 VA, 60 hertz; or

        - 115 kV – 6000 VA, 60 hertz.

  - Combination Current/Voltage Transformers (Metering Units)

Combination Current/Voltage Transformers shall maintain the same electrical, accuracy and mechanical characteristics as individual CTs and VTs.  Physical dimensions may vary according to design.

  - Insulating Oil (if present)

The nameplate shall be of non-corroding material and shall indicate that the dielectric fluid is free of polychlorinated biphenyls by the inscription:

“CONTAINS NO PCB AT TIME OF MANUFACTURE”.

- Testing

The TDSP shall ensure that, before shipment, each transformer is subjected to testing as prescribed by recognized industry standards and other tests including:

        - Applied voltage test for primary and secondary winding withstand to ground;

        - Induced voltage test for proper turn-to-turn insulation;

        - Accuracy test for ratio correction factor and phase-angle verification to confirm 0.3% metering accuracy per recognized industry standards;

        - Ratio test;

        - Insulation Power Factor test;

        - Polarity test;

        - Leak test to assure integrity of gaskets and seals; and

        - Partial Discharge Test may be done in conjunction with applied voltage testing to assure proper line-to-ground withstand.

The tests shall be submitted to the ISO on a formal certified test report.

- Required Information

The following drawings and information shall be required:

        - 3 sets of drawings showing physical dimensions including mounting holes and primary CT terminal details, nameplate.  The TDSP shall ensure that it receives a schematic of connections from its supplier; and

Technical Metering Attachment e:	TRANSFORMER AND LINE LOSS CORRECTION FACTORS

- Introduction

Transformer loss correction refers to the practice of metering electrical Energy delivered at a high-voltage billing point using metering equipment connected on the low-voltage side of the delivery point.  The metering equipment is provided with a means of correction that adds to, or subtracts from, the actual active and reactive metered values in proportion to losses that are occurring in the transformer.

Transformer losses are divided into two parts:

- the core or iron loss (referred to as the no-load loss); and

- the copper loss (referred to as the load loss).

Both the no-load loss and the load loss are further divided into Watts and Var components.

The no-load (iron) loss is composed mostly of eddy current and hystersis losses in the core.  No-load loss varies in proportion to applied voltage and is present with or without load applied.  Dielectric losses and copper loss due to exciting current are also present, but are generally small enough to be neglected.

The load (copper) watt loss (I2 + stray loss) is primarily due to the resistance of conductors and essentially varies as the square of the load current.  The Var component of transformer load loss is caused by the leakage reactance between windings and varies as the square of the load current.

Line losses are considered to be resistive and have I2R losses.  The lengths, spacings and configurations of lines are usually such that inductive and capacitive effects can be ignored. If line losses are to be compensated, they are included as part of the transformer load losses (Watts copper).

The coefficients, which are calculated at the calibration point of the meter, are entered into the meter as Percent Loss Watts Copper %LWCU), Percent Loss Watts Iron (%LWFE), Percent Loss Vars Copper (%LVCU), and Percent Loss Vars Iron (%LVFE).

Percent losses are losses expressed as a percent of the full load on a meter.

The formulas used to determine the compensation values at a particular operating point are:

| WATTS |  | Measured Voltage 2 |  | Measured Current 2 |  |
| --- | --- | --- | --- | --- | --- |
| Compensation | = | ———————————— | * %LWFE + | ———————————— | * %LWCU |
| Value |  | Calibration Point Voltage 2 |  | Calibration Point Current 2 |  |

| Vars |  | Measured Voltage 4 |  | Measured Current 2 |  |
| --- | --- | --- | --- | --- | --- |
| Compensation | = | ———————————— | * %LVFE + | ———————————— | * %LVCU |
| Value |  | Calibration Point Voltage 4 |  | Calibration Point Current 2 |  |

- Calculating Transformer Loss Constants

Transformer Loss correction calculations with electronic meters are accomplished internally with firmware. Various setting information and test data is required to calculate the four values which are to be programmed into the meter.

The following information is required about meter installations:

- the transformer high voltage (HV) voltage rating

- the transformer kVa rating

- the transformer high voltage (HV) tap settings

- the transformer low voltage (LV) tap settings

- the transformer connection (wye or delta)

- the transformer phases (1 or 3)

- the voltage transformer (VT) ratio

- the current transformer (CT) ratio

- the number of meter elements

The following data from a transformer test report is required:

- no-load (iron) loss

- full-load (copper) loss

- percent impedance

- percent excitation current

The test data required may be obtained from the following sources:

- the manufacturer’s test report

- a test completed by a utility or independent electrical testing company

If the transformer bank is used to deliver power to more than one entity (that is, it is a joint use transformer bank) additional data is required, including the:

- maximum available kVa from the transformer bank

- contracted amount of load to be compensated in kW

- contractual power factor amount to be used in calculations

- Calculating Line Loss Constants

Line Loss correction calculations with electronic meters are accomplished internally with firmware. Various information about the radial line is required to calculate the value which is programmed into the meter. The resistance of the conductors are used to calculate a value which is added to the Watts copper loss value which is programmed into the meter. It is not practical to compensate for line losses in a network connected line, only radial lines.

The following information is required about the transmission line:

- the transmission line type

- the ohms per mile

- the length in miles of each type of line

- Applications

Joint Use Transformers

Where a transformer bank is used to deliver power to more than one entity (that is, a joint use transformer bank), no-load iron losses are adjusted by the transformer percent use. This percent use is determined by dividing a negotiated contract kW load (Contract kW) at a negotiated power factor (% Power Factor) by the maximum available kVa from the transformer bank (Max. Available kVa).

Switched Lines

Line Loss correction for radial lines which are switched, must be based on a negotiated average resistance based on the typical operating characteristics.

Transformer Load Tap Changer

Transformers equipped with a load tap changer (i.e., which has the capability to change transformer voltage tap positions or settings under Load) for regulating voltage, must have the corrections calculated at the median tap voltage. Differences in the corrections must be minimal and must even out over time as the bank operates above and below the median tap voltage.

- Worksheets

A pro forma Transformer and Line Loss Correction Worksheet which can be used to perform the above calculation is attached to this Technical Metering Attachment.  Instructions for completing the worksheet are as follows:

- Complete the Name, Delivery, Location and Revision Date fields using the TDSP’s name, operating name, city, state, and the date of the calculation.

- Enter Transformer High Voltage (HV) winding rated voltage, this is the voltage at which the transformer tests were performed.

- Enter the HV and Low Voltage (LV) transformer tap settings.

- Enter ‘Y’ or ‘D’ to indicate the secondary winding connection of either wye or delta.

- Enter ‘1’ to indicate that the transformer bank is comprised of single phase units or ‘3’ to indicate the bank is comprised of three phase units.

- Enter ‘2’ or ‘3’ to indicate the number of elements in the meter.

- Enter the VT and CT ratios of the instrument transformers used in the metering.

- Enter ‘Y’ or ‘N’ to indicate if the transformer bank is utilized by more than one entity.

- Enter the negotiated contract and power factor for the joint use portion of the transformer (if any).

- If compensation coefficients are required at a calibration point other than five amps, enter the new value.

- Space is provided to make comments about the calculation or delivery configuration.

- Enter the manufacturer and serial number of the transformer(s).

- Enter the kVa rating of each bank. For multiple rated banks, the base kVa should be used.  Enter the test data collected at base kVa.

- Enter the no-load losses in Watts from the test data.

- Enter the load losses in Watts from the test data.

- Enter the impedance from the test data.

- Enter the Exciting current from the test data.

- If the maximum available kVa from the transformer bank is more than the rated kVa, this value can be entered manually.  An example may be for a triple rated transformer that has fans with a rating which is more than the base kVa. This value only affects the percent use calculation.

- Enter the line type for each type of line to be compensated.

- Enter the resistance in ohms per mile of each type of line to be compensated.

- Enter the total length in miles of each type of line to be compensated.

- Reference Materials

The following additional references may be referred to for assistance when calculating the correction factors referred to in this Technical Metering Attachment.

- Handbook For Electricity Metering, Ninth Edition. Edison Electric Institute. Washington, D.C.

- Eastern Specialty Company Bulletin No. 63.

- American National Standard Institute. Test Code for Distribution, Power and Regulating Transformers.

- System Loss Compensation, Schlumberger Industries, Quantum Multifunction Meter Hardware Instruction Manual 1610, November 1993.

- Transformer Loss Calculation Method, Process System Manual, Technical Metering Attachment E.

Transformer and Line Loss Correction Worksheet (Example)

TRANSFORMER AND LINE LOSS CORRECTION

Name:		Acme Power Company

Delivery:	Delivery Number 5

Location:	Surf Beach, CA

Rev. Date:	5/6/97

| HV Rated Voltage: | 110000 V | VT Ratio: | 60:1 |
| --- | --- | --- | --- |
| HV Tap: | 101200 V | CT Ratio: | 600:5 |
| LV Tap: | 13090 V | Joint Use (Y/N): | N |
| Trf. Conn. (Y/D): | Y | Metering Trf. Use: | 100 % |
| Trf. Phase (1 or 3) | 3 | Contract kW: | 10,000 kW |
| # Meter Elem.: | 3 | Power Factor: | 95 % |

| Compensation Values (@ 5A F.L.) |  | Compensation Values at: | 10 A |
| --- | --- | --- | --- |
| Watt Fe Loss: | 0.16 % | Watt Fe Loss: | .08 % |
| Watt Cu Loss: | 0.53 % | Watt Cu Loss: | 1.06 % |
| Watt Tot. Loss: | 0.69 % | Watt Tot. Loss: | 1.14 % |
| Var Fe Loss: | 0.31 % | Var Fe Loss: | 0.16 % |
| Var Cu Loss: | 10.96 % | Var Cu Loss: | 21.92 % |
| Var Tot. Loss: | 11.27 % | Var Tot. Loss: | 22.08 % |

Comments:

TRANSFORMER DATA

| Serial Number | KVa Rating | No Load (Fe) Loss | Load (Cu) Loss | (Z) Impedance | (IE) Exciting Current |
| --- | --- | --- | --- | --- | --- |
| ABB 1000001 | 12000 | 22200 w | 51360 w | 8.84 % | 0.45 % |

| Total kVa rating: | 12000 |  | Max Available kVa: | 12000 |
| --- | --- | --- | --- | --- |

LINE DATA

|  | Resistance | Length |
| --- | --- | --- |
| #1 Line Type: | Ohms/mile | miles |
| #2 Line Type: | Ohms/mile | miles |
| #3 Line Type: | Ohms/mile | miles |
| #4 Line Type: | Ohms/mile | miles |
| #5 Line Type: | Ohms/mile | miles |
| #6 Line Type: | Ohms/mile | miles |

Transformer and Line Loss Correction Worksheet (Example, continued)

TRANSFORMER AND LINE LOSS CORRECTION

Name:		ACME Power Company

Delivery:	Delivery Number 5

Location:	Surf Beach, CA

Rev. Date:	5/6/97

| HV Rated Voltage: | 110000 V | VT Ratio: | 60:1 |
| --- | --- | --- | --- |
| HV Tap: | 101200 V | CT Ratio: | 600:5 |
| LV Tap: | 13090 V | Joint Use (Y/N): | N |
| Trf. Conn. (Y/D): | Y | Metering Trf. Use: | 100 % |
| Trf. Phase (1 or 3) | 3 | Contract kW: | 10,000 kW |
| # Meter Elem.: | 3 | Power Factor: | 95 % |

TRANSFORMERS

| Serial Number | KVa |
| --- | --- |
| ABB 1000001 | 12000 |

**TRANSFORMER LOSS COMPENSATION TEST POINTS FOR WATTHOURS**

SERIES TEST

| Test Load | % Iron | % Copper | % Total |
| --- | --- | --- | --- |
| Light | 1.60 | 0.05 | 1.65 |
| Full | 0.16 | 0.53 | 0.69 |
| 0.5 P.F. | 0.32 | 1.06 | 1.38 |

**TRANSFORMER LOSS COMPENSATION TEST POINTS FOR VARHOURS**

SERIES TEST

| Test Load | % Iron | % Copper | % Total |
| --- | --- | --- | --- |
| Light | 3.10 | 1.10 | 4.20 |
| Full | 0.31 | 10.96 | 11.27 |
| 0.5 P.F. | 0.62 | 21.92 | 22.54 |

Pro Forma Transformer and Line Loss Correction Worksheet

TRANSFORMER AND LINE LOSS CORRECTION

Name:

Delivery:

Location:

Rev. Date:

| HV Rated Voltage: | V | VT Ratio: | :1 |
| --- | --- | --- | --- |
| HV Tap: | V | CT Ratio: | :5 |
| LV Tap: | V | Joint Use (Y/N): |  |
| Trf. Conn. (Y/D): |  | Metering Trf. Use: | 100 % |
| Trf. Phase (1 or 3) |  | Contract kW: | kW |
| # Meter Elem.: |  | Power Factor: | % |

| Compensation Values (@ 5A F.L.) |  | Compensation Values at: | 10 A |
| --- | --- | --- | --- |
| Watt Fe Loss: | % | Watt Fe Loss: | % |
| Watt Cu Loss: | % | Watt Cu Loss: | % |
| Watt Tot. Loss: | % | Watt Tot. Loss: | % |
| Var Fe Loss: | % | Var Fe Loss: | % |
| Var Cu Loss: | % | Var Cu Loss: | % |
| Var Tot. Loss: | % | Var Tot. Loss: | % |

Comments:

TRANSFORMER DATA

| Serial Number | KVa Rating | No Load (Fe) Loss | Load (Cu) Loss | (Z) Impedance | (IE) Exciting Current |
| --- | --- | --- | --- | --- | --- |

| Total kVa rating: | Max Available kVa: |
| --- | --- |

LINE DATA

|  | Resistance | Length |
| --- | --- | --- |
| #1 Line Type: | Ohms/mile | miles |
| #2 Line Type: | Ohms/mile | miles |
| #3 Line Type: | Ohms/mile | miles |
| #4 Line Type: | Ohms/mile | miles |
| #5 Line Type: | Ohms/mile | miles |
| #6 Line Type: | Ohms/mile | miles |

Pro Forma Transformer and Line Loss Correction Worksheet (continued)

TRANSFORMER AND LINE LOSS COMPENSATION

Name:

Delivery:

Location:

Rev. Date:

| HV Rated Voltage: | V | VT Ratio: | :1 |
| --- | --- | --- | --- |
| HV Tap: | V | CT Ratio: | :5 |
| LV Tap: | V | Joint Use (Y/N): |  |
| Trf. Conn. (Y/D): |  | Metering Trf. Use: | 100 % |
| Trf. Phase (1 or 3) |  | Contract kW: | kW |
| # Meter Elem.: |  | Power Factor: | % |

TRANSFORMERS

| Serial Number | kVa |
| --- | --- |

**TRANSFORMER LOSS COMPENSATION TEST POINTS FOR WATTHOURS**

SERIES TEST

| Test Load | % Iron | % Copper | % Total |
| --- | --- | --- | --- |
| Full |  |  |  |
| 0.5 P.F. |  |  |  |
| Light |  |  |  |

**TRANSFORMER LOSS COMPENSATION TEST POINTS FOR VARHOURS**

SERIES TEST

| Test Load | % Iron | % Copper | % Total |
| --- | --- | --- | --- |
| Full |  |  |  |
| 0.5 P.F. |  |  |  |
| Light |  |  |  |

Technical Metering Attachment F:	INSTRUMENT TRANSFORMER RATIO AND CABLE LOSS
CORRECTION FACTORS

Background

All current transformers (CTs) and voltage transformers (VTs) (collectively, instrument transformers) have inherent errors due to their design and the physical properties of the materials used in their construction.  These errors are manifested as a magnitude and phase angle difference between the “ideal” nameplate ratio and the waveform actually present on the secondary of the transformer. The terms used to denote these errors are Ratio Correction Factor (RCF) and Phase Angle Correction Factor (PACF).

The burden (load) connected to instrument transformer secondaries has an effect on the RCF and PACF of the units.  All wiring and instrumentation of any kind is part of the burden.  On a CT, the burden is designated in ohms and is represented by a number ranging from B-0.1 through B-1.8.  On a VT, burden is measured in volt-amps and indicated by an alpha character, such as W, X, M, Y, Z or ZZ.  The magnitude of these burdens must be known and kept within specified limits or additional errors will occur in the metering.

Significant impedance in the leads between the VTs and the meter can be another source of error, where a voltage drop in the leads is caused by the load of the meter and any other connected devices between the VTs and the meter.  Conductors which are too small or too long can cause metering error.

Correction when the Burden Rating is exceeded

Where the connected burden of a metering circuit exceeds the burden rating of a CT or VT or if an existing instrument transformer does not meet minimum ISO accuracy requirements, then one of the actions listed below must to be taken:

            - The preferred action is to correct the problem by either replacing the instrument transformer(s) with higher burden rated revenue class units or reducing the burden on the circuit to comply with the name plate of existing instrument transformer(s).

            - An acceptable action is to apply ISO approved correction factors to the meter to adjust the meter’s registration to compensate for inaccuracies.

The TDSP will be responsible for properly calculating and applying the CT/VT and cable loss correction factors to its meter to adjust for inaccuracies in the metering circuit.  ISO approved algorithms and spreadsheets for calculating correction factors are included in this Technical Metering Attachment.

CT Ratio Correction Factor

Current transformers are usually tested by the manufacturer for the value of RCF and phase angle at both 5 and 0.5 amp secondary currents.  The values for each CT in an installation would be averaged together to determine the CT Ratio Correction Factor (RCFI) and CT Phase Angle (b).  If the current transformers used are revenue metering with an accuracy class of 0.3 % and are operated at or below their rated burden, then the correction factors may be disregarded.

VT Ratio Correction Factor

Voltage transformers are usually tested by the manufacturer for the value of RCF and phase angle at rated voltage.  The values for each VT in an installation would be averaged together to determine the VT Ratio Correction Factor (RCFE) and VT Phase Angle (g).  If the voltage transformers used are revenue metering with an accuracy class of 0.3 % and are operated at or below their rated burden, then the correction factors may be disregarded.

Cable Loss Correction Factor

The secondary voltage cables at an installation can be tested to determine the losses and phase angle of each.  These values would then be averaged together to get the Cable Loss Correction Factor (CLCF) and the Phase Angle (a) for the installation.  If the calculated connected burden of each phase do not exceed the VT burden rating, then the correction factors may be disregarded.

Final Correction Factor

The PACF for an installation is determined by the following formula:

Where cosQ is the secondary apparent power factor.

The Final Correction Factor (FCF) can then be determined as follows:

FCF  =  RCFI  *  RCFE  *  CLCF  *  PACF

The Percent Error is the amount of error caused by the instrument transformers and cable loss, it is calculated as follows:

Percent Error  =  (1-FCF)*(100)

The Percent Meter Adjustment is the adjustment to the meter required to compensate for the Percent Error, it is calculated as follows:

Percent Adjustment Factor  =  (FCF-1)*(100)

The FCF is applied to the calibration of the meter, usually through adjustment of the calibration potentiometer or through a change in the programmed calibration values.  After an adjustment to the meter is made, the meter should be tested at all test points to show that the meter is within calibration limits with the calibration values applied.  A FCF which results in a correction of less than 0.6% can be disregarded since this is less than the required combined accuracy of the instrument transformers.  However, if any correction factor (full load, light load or power factor) results in a correction of more than 0.6%, they should all be applied.

Applications

Typical Installation

The preferred meter installation would utilize revenue metering class instrument transformers (0.3 %) operated at or below rated burden. If this is not the case, one or more of the following actions may be used to correct the problem:

- Replace instrument transformers with higher burden rated units.

- Reduce the burden on the circuit to comply with the existing rated burden.

- Apply correction factors to the meter to compensate for inaccuracies.

Paralleling CTs

In normal revenue metering, current transformers would not be paralleled, but there are some applications where paralleling is done because the cost of the installation is reduced and the possibility of reduced meter accuracy is acceptable. A typical installation of this type would be to meter the net output of a generating station on a single meter rather than metering gross generator output and auxiliary power separately. In these type of installations additional rules apply:

- All of the transformers must have the same nominal ratio regardless of the ratings of the circuits in which they are connected.

- All transformers which have their secondaries paralleled must be connected in the same phase of the primary circuits.

- The secondaries must be paralleled at the meter and not at the current transformers.

- There should only be one ground on the secondaries of all transformers. This should be at their common point at the meter.  Each utility may use their established grounding procedures.

- Modern current transformers with low exciting currents and, therefore, little shunting effect when one or more current transformers are “floating” at no load should be used. Three or more “floating” current transformers might have an effect that should be investigated.

- The secondary circuits must be so designed that the maximum possible burden on any transformer will not exceed its rating. The burden should be kept as low as possible as its effects are increased in direct proportion to the square of the total secondary current.

- A common voltage and frequency must be available for the meter.

- If adjustments are made at the meter to compensate for ratio and phase angle errors, the ratio and phase angle error corrections used must represent the entire combination of transformers as a unit.

- The watthour meter must be able to carry, without overload errors, the combined currents from all the transformers to which it is connected.

- While servicing meters and equipment on parallel CT secondaries, all CTs must be by-passed (shorted).  When work is completed all by-passes must be removed.

Worksheets

A worksheet which can be used to perform the above calculations is attached to this Technical Metering Attachment.  Instructions for completing the worksheet follow:

- Complete the Name, Delivery and Location fields using the TDSP’s name, the operating name of the delivery, and the city and state for the location.

- Enter the values of RCF and phase angle as tested at full load and light load for each CT in the circuit. Record the manufacturer and serial number of each transformer.

- Enter the values of RCF and phase angle as tested at rated voltage for each VT in the circuit. Record the manufacturer and serial number of each transformer.

- Enter the values of the Cable Loss Correction Factor and Phase Angle for the secondary voltage cables.

- The worksheet will calculate the Final Correction Factors, Percent Errors and Percent Adjustment Factors to be applied to the meter calibration.

Reference Materials

The following additional reference may be referred to for assistance when calculating the correction factors referred to in this Technical Metering Attachment.

- Handbook For Electricity Metering, Ninth Edition. Edison Electric Institute. Washington, D.C.

CT/VT Ratio and Cable Loss Correction Worksheet (Example)

Name:

Delivery:

Location:

| Full Load | Light Load |
| --- | --- |

CT Test Data:

Phase ‘A’ CT		Mfr. & Serial Number:

| Ratio Correction Factor (RCFI) | 1.0003 | 1.0002 |
| --- | --- | --- |
| Phase Angle () (minutes) | -0.3 | 2.2 |

Phase ‘B’ CT		Mfr. & Serial Number:

| Ratio Correction Factor (RCFI) | 1.0004 | 1.0029 |
| --- | --- | --- |
| Phase Angle () (minutes) | -0.4 | 2.2 |

Phase ‘C’ CT		Mfr. & Serial Number:

| Ratio Correction Factor (RCFI) | 1.0019 | 1.0028 |
| --- | --- | --- |
| Phase Angle () (minutes) | -0.3 | 3.1 |

Average of CT’s		Mfr. & Serial Number:

| Ratio Correction Factor (RCFI) | 1.0009 | 1.0020 |
| --- | --- | --- |
| Phase Angle () (minutes) | -0.3 | 2.5 |

VT Test Data:

Phase ‘A’ VT		Mfr. & Serial Number:

| Ratio Correction Factor (RCFE) | 0.9997 |
| --- | --- |
| Phase Angle () (minutes) | 1.5 |

Phase ‘B’ VT		Mfr. & Serial Number:

| Ratio Correction Factor (RCFE) | 0.9996 |
| --- | --- |
| Phase Angle () (minutes) | 1.5 |

Phase ‘C’ VT		Mfr. & Serial Number:

| Ratio Correction Factor (RCFE) | 0.9997 |
| --- | --- |
| Phase Angle () (minutes) | 1.7 |

Average of VT’s		Mfr. & Serial Number:

| Ratio Correction Factor (RCFE) | 0.9997 |
| --- | --- |
| Phase Angle () (minutes) | 1.6 |

Cable Loss Test Data:

Phase ‘A’

| Ratio Correction Factor (CLCF) | 0.9969 |
| --- | --- |
| Phase Angle () (minutes) | 4.3 |

Phase ‘B’

| Ratio Correction Factor (CLCF) | 0.9949 |
| --- | --- |
| Phase Angle () (minutes) | 4.2 |

Phase ‘C’

| Ratio Correction Factor (CLCF) | 0.9959 |
| --- | --- |
| Phase Angle () (minutes) | 4.7 |

Average Cable Loss Data

| Ratio Correction Factor (CLCF) | 0.9959 |
| --- | --- |
| Phase Angle () (minutes) | 4.4 |

Correction Factors:					Full Load		Power Factor	Light Load

| Avg. Combined Corr. Factor | 0.9964 | 0.9964 | 0.9975 |
| --- | --- | --- | --- |
| Phase Ang Corr Factor (PACF) | 1.0003 | 1.0032 | 1.0001 |
| Final Correction Factor (FCF) | 0.9967 | 0.9996 | 0.9977 |
| Percent Error | + 0.33 | + 0.04 | + 0.23 |
| Percent Meter Adjustment | - 0.33 | - 0.04 | - 0.23 |

CT/VT Ratio and Cable Loss Correction Worksheet

Name:

Delivery:

Location:

| Full Load | Light Load |
| --- | --- |

CT Test Data:

Phase ‘A’ CT		Mfr. & Serial Number:

| Ratio Correction Factor (RCFI) |  |  |
| --- | --- | --- |
| Phase Angle () (minutes) |  |  |

Phase ‘B’ CT		Mfr. & Serial Number:

| Ratio Correction Factor (RCFI) |  |  |
| --- | --- | --- |
| Phase Angle () (minutes) |  |  |

Phase ‘C’ CT		Mfr. & Serial Number:

| Ratio Correction Factor (RCFI) |  |  |
| --- | --- | --- |
| Phase Angle () (minutes) |  |  |

Average of CT’s		Mfr. & Serial Number:

| Ratio Correction Factor (RCFI) |  |  |
| --- | --- | --- |
| Phase Angle () (minutes) |  |  |

VT Test Data:

Phase ‘A’ VT		Mfr. & Serial Number:

| Ratio Correction Factor (RCFE) |  |
| --- | --- |
| Phase Angle () (minutes) |  |

Phase ‘B’ VT		Mfr. & Serial Number:

| Ratio Correction Factor (RCFE) |  |
| --- | --- |
| Phase Angle () (minutes) |  |

Phase ‘C’ VT		Mfr. & Serial Number:

| Ratio Correction Factor (RCFE) |  |
| --- | --- |
| Phase Angle () (minutes) |  |

Average of VT’s		Mfr. & Serial Number:

| Ratio Correction Factor (RCFE) |  |
| --- | --- |
| Phase Angle () (minutes) |  |

Cable Loss Test Data:

Phase ‘A’

| Ratio Correction Factor (CLCF) |  |
| --- | --- |
| Phase Angle () (minutes) |  |

Phase ‘B’

| Ratio Correction Factor (CLCF) |  |
| --- | --- |
| Phase Angle () (minutes) |  |

Phase ‘C’

| Ratio Correction Factor (CLCF) |  |
| --- | --- |
| Phase Angle () (minutes) |  |

Average Cable Loss Data

| Ratio Correction Factor (CLCF) |  |
| --- | --- |
| Phase Angle () (minutes) |  |

Correction Factors:					Full Load		Power Factor	Light Load

| Avg. Combined Corr. Factor |  |  |  |
| --- | --- | --- | --- |
| Phase Ang Corr Factor (PACF) |  |  |  |
| Final Correction Factor (FCF) |  |  |  |
| Percent Error |  |  |  |
| Percent Meter Adjustment |  |  |  |

Technical Metering Attachment G:	ISO DATA VALIDATION, ESTIMATION
AND EDITING PROCEDURES

This Technical Metering Attachment is provided for information purposes only, it gives an overview of the procedures that the ISO will use to validate, edit and estimate EPS Meter Data and, where an exemption applies, Meter Data received from TDSPs.

Note: This procedure will be the Uniform Business Practices process for VEE once it has been finalized.