| PRR Number | 493PRR | PRR Title | Induction Generator Exemption |
| --- | --- | --- | --- |
| Recommended Action |  | Approve as revised |  |
| Protocol Section(s) Requiring Revision (include Section No. and Title) |  | 6.5.7.1(7), Generation Resources Required to Provide VSS Installed Reactive Capability |  |
| Proposed Effective Date |  | Upon filling ERCOT staffing requirements |  |
| Priority & Rank Assigned |  | N/A |  |
| Summary of Impact Analysis |  | No impacts to ERCOT computer systems; 0.5 FTE required in transmission planning prior to implementation, an additional 0.10 FTE also needed in Compliance that can be absorbed by current staffing; minor business process impacts; no grid operations impacts. |  |
| Revision Description |  | Revise section within the Reactive Standards to clarify the mechanism an induction generator may use to receive an exemption from the VSS installed reactive capability requirements and the level of the payment to be made. |  |
| Benefit |  | See revision description. |  |
| PRS Recommendation |  | PRS recommends approval of PRR493 as revised by ERCOT comments and PRS. |  |
| TAC Recommendation |  | TAC recommends approval of PRR493 as recommended by PRS. |  |

| Sponsor |  |
| --- | --- |
| Name | Richard Ross |
| E-mail Address | rross@aep.com |
| Company | AEP |
| Company Address | 2 West 2nd Street Tulsa, OK 74137 |
| Phone Number | (918) 594-2906 |
| Fax Number | (866) 947-1796 |

ERCOT/Market Segment Impacts and Benefits

|  | Impact |  | Benefit |
| --- | --- | --- | --- |
|  | Business | Computer Systems |  |
| ERCOT | None | None | Clarifies procedure for receiving and the cost of exemption for induction generators. |
| MARKET SEGMENT | None | None | None |
| Consumer | None | None | Assures that the cost of installing equipment to replace the Reactive Power not being provided by the induction generator is comparable to the cost being paid for the exemption, so that exemptions are neutral with respect to Transmission Cost of Service. Lays the foundation that this cost is subject to change in the future as construction costs and/or technology changes. |
| LSE: General, Including NOIE | None | None | Same as consumer. |
| LSE: CR & REP | None | None | Same as consumer. |
| QSE | None | None | None |
| Resource | None | None | Same as ERCOT. |
| TDSP | None | None | Same as consumer. |

Proposed Protocol Language Revision

## {The baseline language shown below was implemented on March 1, 2004.}

## 6.5	Technical Requirements for Providers of Ancillary Services

6.5.7	Voltage Support Service

6.5.7.1	Generation Resources Required to Provide VSS Installed Reactive Capability

- Generation Resources required to provide VSS must be capable of producing a defined quantity of Reactive Power at rated capability (MW) to maintain a Voltage Profile established by ERCOT.  This quantity of Reactive Power is the Unit Reactive Limit (URL).

- Generation Resources required to provide VSS whose installations were in operation on September 1, 1999 or later, except as noted below, shall have and maintain a URL which has an over-excited (lagging) power factor capability, of ninety-five hundredths (0.95) or less and an under-excited (leading) power factor capability of ninety-five hundredths (0.95) or less, both determined at the generating unit's maximum net power to be supplied to the transmission grid and at the transmission system Voltage Profile established by ERCOT, and both measured at the point of interconnection to the TDSP.

- Qualified renewable Generation Resources (as described in Section 14, Renewable Energy Credit Trading Program) in operation before February 17, 2004, required to provide VSS and all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999 whose current design does not allow them to meet the URL as stated above, will be required to maintain a  URL that is limited to the quantity of Reactive Power that the Generation Resource can produce at it’s rated capability (MW) as determined using procedures and criteria described in the Operating Guides.

- New generating units connected before May 17, 2005, whose owners demonstrate to ERCOT’s satisfaction that design and/or equipment procurement decisions were made prior to February 17, 2004, based upon previous standards, whose design does not allow them to meet the URL as stated above, will be required to maintain a URL that is limited to the quantity of Reactive Power that the Generation Resource can produce at its rated capability (MW) as determined using procedures and criteria described in the Operating Guides

- Upon request to, and with the approval of ERCOT, multiple generating units connected to the same transmission bus may be treated as a single generating unit for the purposes of these URL requirements only.

- Upon submission by a Generation Resource required to provide VSS to ERCOT of a specific proposal for requirements to substitute for these URL requirements, ERCOT shall either approve such alternative requirements or provide the submitter an explanation of its objections to the proposal.  Alternative requirements may include supplying additional static and/or dynamic Reactive Power capability as necessary to meet the area’s Reactive Power requirements.

- Reserved

[PRR493:  Replace item (7) above upon filling ERCOT staffing requirements.]

(7)	An induction generator may elect to make a contribution in aide of construction in lieu of meeting the installed capacity VSS requirements contained herein.  In order to comply with the VSS requirements under this Section, 6.5.7.1 (7), the generator must make payment to the interconnecting TDSP under its generation Interconnection Agreement in a manner similar to that used to collect payments for the direct assignment of interconnection Facilities under applicable PUCT rules.  The level of payment shall reflect the cost to the TDSP of procuring, installing, operating, and maintaining any Reactive Power equipment required to replace the Reactive Power capability that otherwise would be necessary for the interconnection of the generator.  In order for this Section 6.5.7.1(7) to be effective for VSS compliance, the TDSP shall certify to ERCOT that the induction generator has complied with these requirements.

- For Generation Resources required to provide VSS, no unit equipment replacement or modification shall reduce the capability of the unit below the requirements to be met by that unit prior to the replacement/modification, unless specifically approved by ERCOT.

- Generation Resources required to provide VSS shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT (conveyed by way of their QSE) unless equipment damage is imminent.

| PRR Evaluation |  |
| --- | --- |
| Non-ERCOT Market Comparison | No Comparison conducted. |
| Comments Author | Comments Summary |
| ERCOT | Clarifications. |

| Sponsor's Revision Description | Revise section to clarify the mechanism an induction generator may use to receive an exemption from the generator and the level of the payment to be made. |
| --- | --- |
| Sponsor's Reason for Revision | See revision description. |