## Updated Event Code Matrix
Meter vs. MV90 Event codes
*** UPDATED Listing 1-28-04 ***
EVENT | METER
| ION | Mark V | Q1000
Hardware Errors | Various | Various | Various
Firmware Errors | Various | Various | Various
RAM and ROM Errors | NA - See Note 1 | 6 | OA
Clock Errors | NA | NA | 17
Pulse Overflow Errors | DC | 2C | NA
Low Battery Condition | CA | 1 | NA
AC Power Up | OE | NA | NA
AC Power Down | OD | OD | OD
Cold Start (re-init to MFG Specs) | D4 | D4 | NA
Warm Start (init register data only) | NA | NA | NA
Configuration Changed | 12 | 12 | 12
Clock Set/Change | 15, 16 | 6B | 6B or 85
Test Mode Activation | 51,52 - See Note 2 | 51, 52 | 51, 52
Inactive Potential | A0, A1, A2 | A0, A1, A2 | NA
| NA | = No Code in MV90's TIM
| Note 1 | = Under review by Power Measurement for relevancy
| Note 2 | = Added to TIM by ITRON/Power Measurement
Note on B17: ERCOT: Removed by Itron 6/26/01 because they could not distinguish between Test Mode and someone pressing "Enter" o front panel.
Note on C4: ERCOT: Firmware Ver 4.0 or later

## ION
Conversion of IONTM events to MV-90 events
EFFECT VALUE | EFFECT HANDLE | MV-90-EVENT | MV-90 EVENT CODE
Power down |  | Power outage, short int | 0D
Power up |  | Power outage, short int | 0E
Time about to be changed |  | Time reset occurred | 15
Time changed |  | Time reset occurred | 16
9011 |  | Watchdog timeout | 0C
Battery low |  | Battery fail | CA
Master reset complete |  | Reset occurred | D4
54608 |  | Program malfunction detected | 3
700 |  | Modem failure | 98
Meter password change |  | Password changed | 13
Pulsed |  | Billing reset | 45
On | 61DDh | Meter over Kw demand | 2C
On | 61E1h | Meter over voltage unbalance | D5
On | 61DEh | Meter over threshold phase a | DC
On | 61DFh | Meter over threshold phase b | DC
On | 61E0h | Meter over threshold phase c | DC
On | 6063 | Potential voltage loss on (phase not listed) | EB
On | 6064 | Potential voltage loss on (phase not listed) | A0
On | 6065 | Potential voltage loss on (phase not listed) | A1
On | 6066 | Potential voltage loss on (phase not listed) | A2
On | 6063 | Voltage sag | E6
On |  | Voltage imbalance | D5
Disturbance |  | Power quality event start | E2
Normal |  | Power quality event end | E3
Partial factory init |  | Configuration changed | 12
Hardware security |  | Password changed | 13
Hardware security enabled |  | Password changed | 13
Changed setup |  | Configuration changed | 12
DST started |  | Fall daylight savings time change | 18
DST on |  | Fall daylight savings time change | 18
Time sync |  | Recorder clock set new time | 16
Time change |  | Recorder clock set new time | 16
|  | Output control relay toggle | 44
Password security en |  | Changed password
Telnet locked out |  | Attempted access with invalid password
Value changed |  | Operating parameter changed
Unknown - text event
Test Mode Activated |  | Test Mode Activated | Added to TIM by ITRON/Power Measurement

## Mark V
MARK V EVENT CODE MAP
Transdata EMS 50/ MARK V Firmware Version 4.0 or later only
TRANSDATA MARK V EVENT | MV90 EVENT | MV90 Event Code
Voltage Sag- Phase A | Voltage Sag | E6
Voltage Sag- Phase B | Voltage Sag | E6
Voltage Sag- Phase C | Voltage Sag | E6
Voltage Swell - Phase A | Voltage Swell | E7
Voltage Swell - Phase B | Voltage Swell | E7
Voltage Swell - phase C | Voltage Swell | E7
Voltage Outage - Phase A | Potential A Inactive | A0
Voltage Outage - Phase B | Potential C Inactive | A2
Voltage Outage - Phase C | Potential B Inactive | A1
Breaker Operation - Phase A | Breaker Operation | E8
Breaker Operation - Phase B | Breaker Operation | E8
Breaker Operation - Phase C | Breaker Operation | E8
Volt. Under Limit - Phase A | Low Voltage Limit | E9
Volt. Under Limit - Phase B | Low Voltage Limit | E9
Volt. Under Limit - Phase C | Low Voltage Limit | E9
Angle Outside Limit - Ph A | Phase Angle Limit | EA
Angle Outside Limit - Ph B | Phase Angle Limit | EA
Angle Outside Limit - Ph C | Phase Angle Limit | EA
Cur Below Limit - Phase A | Low Current Limit | EB
Cur Below Limit - Phase B | Low Current Limit | EB
Cur Below Limit - Phase C | Low Current Limit | EB
PF Outside Limit - Phase A | Power Factor Limit | EC
PF Outside Limit - Phase B | Power Factor Limit | EC
PF Outside Limit - Phase C | Power Factor Limit | EC
Ex input 1 Open (hi) | Status Input Opening - # | 32
Ex Input 1 Closed (lo) | Status Input Closure - # | 31
EX input 2 Open(hi) | Status Input Opening - # | 32
Ex input 2 Closed (lo) | Status Input Closure - # | 31
Control Output 1 Open | Relay Opened - Relay # | 36
Control Output 1 Closed | Relay Closed - Relay # | 84
Control Output 2 Open | Relay Opened - Relay # | 36
Control Output 2 Closed | Relay Closed - Relay # | 84
Control Output 3 Open | Relay Opened - Relay # | 36
Control Output 3 Closed | Relay Closed - Relay # | 84
Control Output 4 Open | Relay Opened - Relay # | 36
Control Output 4 Closed | Relay Closed - Relay # | 84
Control Output 5 Open | Relay Opened - Relay # | 36
Control Output 5 Closed | Relay Closed - Relay # | 84
Battery Time Over Limit | Battery Failure | 1
EPROM Diagnostic Error | EPROM Failure | 9D
RAM Diagnostic Error | RAM Error Detected | 6
Register Watchdog Tripped | Watchdog Timer Error | 0C
A/D Watchdog Activated | Watchdog Timer Error | 0C
Communications Error | Communications Session Interrupted | 43
Dial Out Unsuccessful | Call-in Failure | 20
Meter Power Turned off | AC Power Down | 0D
Maximum Demand Reset | Billing Reset | 45
Recorder Data Retrieved | Data Log Uploaded | 8C
Register programmed | Configuration Changed | 12
Time Changed | Time or Date Changed | 6B
Register reading changed | Pre-Set Register Values | 5C
A/D Programmed /recalibrated | Calibration Change | ED
Test Mode Initiated | Start of Test Mode | 51
Test Mode Exited | End of Test Mode | 52
Daylight Savings Time | Unrecognized recorder Event Code/ Spring Daylight Savings Time changed/ Fall daylight Savings Time Changed | 74/19/18
Recorder Time Sync | Recorder time Sync. | EE
TOU Season Change | Season Change | EF
Register Rollover | RAM Buffer Overflow/Initialization | 0A
Demand register overflow | RAM Buffer Overflow/Initialization | 0A
Recorder Overflow | RAM Buffer Overflow/Initialization | 0A
Demand over limit - start | Meter Over Threshold – Channel # | 2C
Demand Over Limit End | Meter Return Within Limits – Channel # | B9
Harmonic Alarm - start | Customer Alarm 1 | 75
Harmonic Alarm - END | Customer Alarm 1 | 75
Event Log Data Retrieved | Event Log Uploaded | 8D
All Meter Data Reset | Metering Equipment Reset | D4
Any Other Event | Unrecognized Recorder Event Code | 74

## Q1000
Q1000 Event Code Map
Manufacturers Description | MV90 Message | MV90 Event Code
MASS_MEM1_EOI | RAM Buffer Overflow/Initialization | ‘0A’
MASS_MEM2_EOI | RAM Buffer Overflow/Initialization | ‘0A’
DEMAND_RESET | Operating Parameter changed | ‘11’
LOSS_OF_PHASE | Phase Failure | ‘D6’
LOSS_OF_PHASEA | Phase Drop-out(Phase, short/Long) | ‘DB’
LOSS_OF_PHASEB | Phase Drop-out(Phase, short/Long) | ‘DB’
LOSS_OF_PHASEC | Phase Drop-out(Phase, short/Long) | ‘DB’
REGISTER_FREEZE | Freeze Meter Readings | ‘47’
CLCOK_ERROR | Recorder Clock Malfunction Detected | ‘17’
ENTER_TEST_MODE | Start of Test Mode | ‘51’
LEAVE_TEST_MODE | End of Test Mode | ‘52’
POWER_OUTAGE | AC Power Down | ‘0D’
CALL_ON_SCHEDULE | Scheduled Call-in | ‘95’
METER_REPROGRAM | Configuration Changed | ‘12’
CLOCK_ADJUSTMENT | Time or Date Changed | ‘6B’
ALARM1_ON | Customer 1 Alarm | ‘75’
ALARM2_ON | Customer 2 Alarm | ‘76’
ALARM3_ON | Alarm Activated | ‘89’
ALARM4_ON | Alarm Activated | ‘89’
ALARM5_ON | Alarm Activated | ‘89’
ALARM6_ON | Alarm Activated | ‘89’
ALARM7_ON | Alarm Activated | ‘89’
ALARM8_ON | Alarm Activated | ‘89’
ALARM9_ON | Alarm Activated | ‘89’
ALARM10_ON | Alarm Activated | ‘89’
ALARM11_ON | Alarm Activated | ‘89’
ALARM12_ON | Alarm Activated | ‘89’
ALARM13_ON | Alarm Activated | ‘89’
ALARM14_ON | Alarm Activated | ‘89’
ALARM15_ON | Alarm Activated | ‘89’
ALARM16_ON | Alarm Activated | ‘89’
ALARM17_ON | Alarm Activated | ‘89’
ALARM18_ON | Alarm Activated | ‘89’
ALARM19_ON | Alarm Activated | ‘89’
ALARM20_ON | Alarm Activated | ‘89’
ALARM21_ON | Alarm Activated | ‘89’
ALARM22_ON | Alarm Activated | ‘89’
ALARM23_ON | Alarm Activated | ‘89’
ALARM24_ON | Alarm Activated | ‘89’
EXTERNAL_INP0_ON | Status Input Opening | ‘6E’
EXTERNAL_INP1_ON | Status Input Opening | ‘6E’
EXTERNAL_INP2_ON | Status Input Opening | ‘6E’
EXTERNAL_INP3_ON | Status Input Opening | ‘6E’
EXTERNAL_EOI | Status Input Opening | ‘6E’
BEFORE_DST_ENTRY | Spring DST Change | ‘19’
AFTER_DST_ENTRY | Spring DST Change | ‘19’
BEFORE_DST_EXIT | Fall DST Change | ‘18’
AFTER_DST_EXIT | Fall DST Change | ‘18’
INVALID_PASSWORD | Attempted Access With Invalid Password | ‘1E’
AUTO_TIME_ADJUST | Auto Timeset Performed | ‘85’
| Unrecognized Recorder Event Code | ‘74’