## Sheet1
Site | Test Date | Date of access | Issue With FOCT | Equipment Affected | Duration | Estimated Data
Site A | P.E. | 2002-09-03 | Cleaned & polished C phase | C phase fiber optic cable | 9/3/02 1316-1445 | 9/3/02 1316-1445
| Letter |  | optic cable
Received
|  | 2002-10-14 | Cleaned & polished optic | Fiber optic cables | 10/24/02 1016-17-15 | 10/24/02 1016-17-15
cable at electronic module
|  | 2003-03-11 | Cleaned & polished optic | Fiber optic cables | 2 day access | Plant shutdown
cable
|  | 2003-06-24 | Replaced C phase optic | C phase fiber optic cable | 6/24/03 1246-1330 | 6/24/03 1246-1330
cable
|  | 2003-08-27 | Replaced optic cables | Fiber optic cables | 1 day access | 7/14/03-8/27/03
|  | 2003-10-01 | Checked cables due to | Fiber optic cables | 10/1/03 1316-1445 | 10/1/03 1316-1445
alarms
| 2003-10-24 | 2003-11-04 | Replaced Fiber Optic CTs | Replaced Fiber Optic CTs | 11/4/03 0731-1700 | Plant shutdown
Site B | 2000-08-23 | 2003-07-21 | Failure A phase optic cable | A phase fiber optic cable | 2003-07-21 | 7/21/03-81/03
|  |  | Failure B phase optic cable | B phase fiber optic cable | 2003-08-01 | 2003-10-14
|  | 2003-10-14 | A phase optic cable replaced | A phase optic cable replaced | 10/14/03- present | 10/14/03- present
Site C | 2001-03-14 | 2003-05-06 | Cleaned & polished A phase | A phase fiber optic cable | 5/6/03 1131-1145 | 5/6/03 1131-1145
cable
|  | 2003-05-27 | Cleaned & polished A phase | A phase fiber optic cable | 1 day access | 1 day access
cable
|  | 2003-06-19 | Replaced optic cables | Fiber optic cables | 6/19/03 0946-1315 | 6/19/03 0946-1315
|  | 2003-09-23 | Fiber Optic CTs found to be | Fiber Optic CTs | 9/23/03-11/5/03 | 9/23/03- 11/5/03
outside of accuracy limits.
were replaced on 11/5/03
Site D | 2000-11-28 | 2003-04-25 | Fiber Optic CTs found to be | Fiber Optic CTs | 1 day access | 1/1/02- 4/25/03
outside of accuracy limits.
were replaced on 4/25/03
Site E | 2001-02-14 | 2002-05-31 | Checked cables due to | Fiber optic cables | 5/31/02 1216-1430 | 5/31/02 1216-1430
alarms
|  | 2002-06-04 | Used spare optic cable on | C phase fiber optic cable | 6/4/02 1501-1515 | 6/4/02 1501-1515
C phase
|  | 2002-10-16 | Checked cables due to | Fiber optic cables | 10/14/02 -10/31/02 | 10/14/02 -10/31/02
alarms
|  | 2002-10-31 | Checked cables due to | Fiber optic cables | 10/31/02- 11/2/02 | 10/31/02- 11/2/02
alarms
|  | 2002-11-02 | Checked cables due to | Fiber optic cables | 11/2/02-11/22/02 | 11/2/02-11/22/02
alarms
|  | 2002-11-22 | Replaced optic cable | Fiber optic cables | 11/22/02 0001-1245 | 11/22/02 0001-1245
Site F | 2001-05-23 | 2002-06-14 | Changed electronics module | electronics module | 6/12/03- 6/14/03 | 6/12/2002- 6/14/02
Site Docs.
Site G | not received | 2002-12-19 | Faulty B phase Amplifier | B phase Amplifier | 12/19/02 0046-1615 | 12/19/02 0046-1615
Site Docs.
Site H | not received | 2003-01-31 | Failed Amplifier | Failed Amplifier | 12/29/01- 2/1/02 | 12/29/01- 2/1/02
Site | Test Date | Date of access | Issue With CCVT | Equipment Affected | Duration | Estimated Data
Site Docs.
AA | not received | 2003-12-05 | CCVT found to be outside | CCVTs | 5/9/2001-present | 5/9/2001-present
of accuracy limits