ERCOT Meter Working Group Meeting

Agenda

Meeting Date: January 28, 2004

Location: ERCOT Taylor, TX

Conference Room 252

9:00 – 9:30: 	Coffee & Donuts (upstairs Lobby outside of Rm 252)

9:30 – 9:45: 	Reading of ERCOT Anti trust rules.

Chairperson read the Antitrust admonition and distributed the Antitrust Guidelines for Members of ERCOT Committees to the MWG.

9:45 – 10:00: 	Opening Business from Chairman

10:00 – 10:30:	Nominations and Voting for Chair and Vice – Chair of the Committee 			2004.

New Chair - Dale Tinnin – CenterPoint Energy

Vice Chair - Ken Swift - ONCOR

ERCOT will follow up with WMS Chair regarding how to submit the nominations to	WMS for confirmation/approval.

10:30 – 10:45: Break.

10:45 – 11:45:	Pat Vinton discussion on Event Logging & MV-90 and TDSP update on 			their discussions with Meter Manufacturers.

Assigned Utilities will research the assigned meters with the manufacturers to resolve the issues on the error codes needed for settlement metering MV90 system (ERCOT). Project assignment due date will be 4/1/2004 to report back to ERCOT.

Herman Millican AE and John Slaughter CPS – Q1000

Ken Swift ONCOR - PML IONs

Dale Tinnin CenterPoint Energy – TransData Mark V

11:45 – 12:45: Lunch

12:45 – 13:15: Presentation from ERCOT on the MOCT’s and CCVT’s Failure History.

Tony Davis

ERCOT concerns of high failure rate of MOCT’s based on information captured via documentation sent in for EPS metering, MV90.

13:15 – 14:00: TDSP Discussion on Field Experience with MOCT’s and CCVT’s

Dale Tinnin

Mark Rollins

Q1 Why is failure rate high?

Manufacturer defects in optical sensors, power supplies and amplifier cards.

Installation errors

Mis-application of equipment by manufacturer

Bugs during new technologies and implementation period

(Mainly Manufacturer 1)

Manufacturer 2 – Temperature sensitive cables.

Q2 Is 5 years test frequency enough?

At this time, MWG saw no reason to change the test frequency. This is a new product and field modifications are being made based on manufacturer’s recommendations. Pending the results from modifications and manufacturer’s suggested improvements a decision will be made at a future date. ERCOT will be maintaining the list of MOCT’s and CCVT’s failures that they are made aware of.

Note: Whenever there is a meeting with the MWG and vendors are present, the vendors will be asked to leave during discussions   about specific products.

14:00 – 14:15: Break

14:15 – 15:15: TDSP Discussion on Field Experience with MOCT’s and CCVT’s (cont.)

Ken Swift

Herman Millican

Q1. What is the TDSPs experience with CCVT’s that are or have been in use for EPS metering?

Drift has occurred on older CCVT’s, recently manufactured ones are stable. ERCOT will volunteer to keep records of failures and testing data (manufacture or TDSP) if supplied.

15:15 – 15:30: Wrap up

ERCOT requested and MWG agreed that for deactivation of an EPS site the following shall be provided to ERCOT by the TDSPs:

- Cutover Form

- The last Site Certifications Form with “Site Deactivation in the comment box, signed by the approved TDSP Inspector with time and date.

- A call in to the MDAS group for the final meter read.