ERCOT Meter Working Group Meeting

Agenda

Meeting Date: June 29, 2004

Location: ERCOT Austin MET Center

Conference Room 206A

Minutes

9:30 – 9:35: 	Reading of ERCOT Anti trust rules.

9:35 – 9:45: 	Opening Business from Chairman – Dale Tinnin

9:45 – 10:45:	Ken Swift – Subject: Adjusting Redundant Meter Validations.

Question to the Group: When units are not operating at full capacity, 			should ERCOT adjust redundant meter validations?

- Pat Vinton made a presentation on Redundant Metering Validations Checks.

Default settings ERCOT uses in the calculations are +/- 2.3% * Site Capacity (MW) listed on Design Proposal. However, if a Peak has been reached that is higher then the Design Proposal Capacity, the new Peak will be used in the calculation.

- TDSPs had concerns about the adequacy of validation checks on the sites that were running below the site capacity listed on the design proposals.

- ERCOT will provide a spreadsheet which will list the current settings along with the previous year peak demand derived from the EU44 report. This report will be sent to the TDSPs by the end of August.

- Each TDSP will review the spreadsheet provided by ERCOT and recommend any changes to the peak demand.

- ERCOT will provide a EU44 report for any meter point if requested by the TDSP.

Power Point Included.

10:45 – 11:00: Break.

11:00 – 11:30:	Ken Swift – Subject: Definition of “Supervision” of EPS Metering Sites.

Question to the Group: From the Protocols – 10.2.3.1. (2) “TDSPs shall 			have EPS metering Facilities installed and maintained under the 				supervision of a TDSP EPS Meter inspector, which is defined as an 			employee or agent of the TDSP who has received EPS training from 			ERCOT, and is described further herein;”

Can any EPS meter work be supervised from the office by a certified EPS 			Meter inspector? If yes,

a) What should be the qualification of the person doing the field work?

b) What processes should be followed when the field work is being 			supervised from the office?

- After discussion, the Meter Working Group (MWG) was not in favor of allowing remote supervision by a certified TDSP inspector for work being conducted on an EPS site by a technician that was not a certified EPS meter inspector.

- TDSP can request a temporary exemption on a case by case basis.

11:30 – 12:00 Submission of Electronic Documentation:

- ERCOT will accept legible scan copies of any certification documentation other than drawings as long as the TDSP retains the originals. This is not an ERCOT requirement but an option available to the TDSPs.

- ERCOT will inspect the originals during the site audits.

- ERCOT will accept an electronic copy of the meter program file (format either .txt or .pdf).

- The following items will need to be typed or written (if scanned) into the program file, front page RH side:

  - Meter Serial number (if not listed elsewhere)

  - Programming Date (if it does not match what’s listed on the program file)

  - Date emailed to ERCOT

  - Meter Inspector name

12:00 – 13:00: Lunch

13:00 – 13:45: Pat Vinton – Subject: Follow up discussion on Event Logging & MV-90 			and TDSP update on their discussions with Meter Manufacturers.

Minutes from previous meeting on the subject:

Assigned Utilities will research the assigned meters manufactures the error codes needed for settlement metering MV90 system (ERCOT). Project assign due date will be 4/1/2004 to report back to ERCOT.

Herman Millican AE and John Slaughter CPS – Q1000

Ken Swift ONCOR - PML IONs

Dale Tinnin CenterPoint Energy – TransData Mark V

- Pat updated Event Code spreadsheet based on TDSPs updates from meter manufactures.

- Open issues will be resolved by the TDSPs and the meter manufactures.

Follow up (see attached Event Code Sheet).

13:45 – 14:30: Don Tandon – Subject: Review and comments on the 					ERCOT Site Audit Check List

- ERCOT presented the Audit Check List.

- TDSPs will send any comments to ERCOT by July 29, 2004.

- The MWG decided that the initial audits will be done utilizing the attached draft Audit Check List. List can be modified based on field experience.

- ERCOT will complete at least three audits this year.

- ERCOT requested that each TDSP review their PPE and Security procedures and send them to ERCOT within a month. ERCOT will only be an observer.

14:30 – 14:45: Break

- Most of TDSPs volunteered their sites for initial audits and ERCOT will work with them for the first audits.

- Sites will be randomly selected with a primary and backup list for 2005. The list will be sent before the end of this year to the TDSPs for planning and approval.

14:45 – 15:20: (con’t) Don Tandon – Subject: Review and comments on 					the ERCOT Site Audit Check List

New Business:

- Ken Swift requested that MDAS provide a tracking number for the 12 hr and 5 day notifications

- Pat Vinton will look into this and get back to the MWG.

- Dale Tinnin discussed load splitting with the group.

15:20 – 15:30: Wrap up