July 29, 2026

Mr. John Slavik

Oncor

115 W. 7th St.

Fort Worth, TX   76102

Dear John,

Power Measurement is writing this letter in response to Oncor and ERCOT’s request for clarification on the ION meter’s compliance to the list of event codes that are required for MV-90.

The attached spreadsheet provides a list of the required event codes and an explanation of how the ION 8000 series meter provides the necessary information for reporting on the events.  The ION 8000 series is fully compliant to the required event code list, however, two events in particular are in question:  RAM/ROM Errors and Clocks Errors.

- RAM/ROM Errors:

If the ION 8000 series meter experiences a significant error that affects the RAM or ROM segment in the meter, the meter will either:

  - Report a non-catastrophic RAM/ROM error as a 54608/600 error sequence, which can then be identified in MV-90 as error code “3” and be successfully reported to Oncor and ERCOT. The attached spreadsheet indicated this event code classification.

OR

  - Shut down in the event of a catastrophic failure without the ability to restart. This is a significant event as a result of a memory failure.  In this case, the error reporting is unnecessary because the meter will not be communicating and the meter will need to be returned on an RMA to Power Measurement.

- Clock Errors:

The internal clock on ION 8000 series meter is an integral component in the main processor of the meter.  The oscillator on the main processor is the main timing/clock source for the all the electronics on the meter. In the event of a catastrophic clock error, the meter shuts downs without the ability to restart. In this case, the error reporting is unnecessary because the meter will not be communicating and the meter will need to be returned on an RMA to Power Measurement.

When the meter is powered down it uses a battery to keep the clock running.  If the meter is powered down when the battery is dead, the meter time will be affected.  Consequently, the “Battery Low” event has the potential to affect the time accuracy of the meter.  This battery event is reported as “CA” in MV 90.

Please note, event reporting for time-synchronization, time drift, or time changes are already provided, as indicated in the attached spreadsheet.  MV-90 can easily rectify any time-synchronization or time-drift errors on the ION meters.  The clock errors described above are in a catastrophic event class, outside the realm of standard timing issues, and are handled differently by the ION 8000 series meter.

Please refer to the attached spreadsheet for the complete list of event codes supported by the ION 8000 series meters. If you should have any questions or comments, please let me know.

Sincerely,

Paul Doig

Power Measurement

Utility Market Segment Manager