## Slide 1: REDUNDANT METERING
  Meter Working Group
  06-29-2004
  Pat Vinton

## Slide 2: What is Purpose of Check?
By comparing interval values between a “PRIMARY” meter and a designated “BACKUP” meter, hardware/software metering errors may be identified
  Loss of phase board, clock circuit, etc…
  Wiring problems
  CT/PT issues (if on different sets of CT/PTs)
  Programming issues

## Slide 3: How Does The Check Work?
Compares, on an Interval-by-Interval basis, the KW (demand) values between a “PRIMARY” meter and a designated “BACKUP” meter.

## Slide 4: What are the Options?
There are two (2) options
  “Channel Tolerance %”
  “Absolute Difference” (in KW)
The “Channel Tolerance %” method does not work well when the pulses/energy per interval are low
  Example: Tolerance % set to +/-5%. If one meter has 10 pulses and another meter has 9 pulses, then when the KW is calculated, there is a 10% difference and the check will fail
ERCOT uses the “Absolute Difference” option, defined in Channel Master File, as its’ tolerance
  This is the ‘Absolute Difference’ (in KW) the two (2) meters can differ and pass Validation

## Slide 5: ERCOT’s Calculations
Factors ERCOT uses in Calculations are:
  Meter Point Capacity
  Meter Uncertainty
  Allowable Time Drift of Meters
  Transformer Uncertainties (PT and CT)

## Slide 6: ERCOT’s Calculations
Meter Point Capacity x (meter uncertainties + allowable time drift between meters + CT uncertainty + PT uncertainty)
  CT and PT uncertainties can be ignored if BOTH meters share the same transformers as any error will effect both meters in the same direction

## Slide 7: ERCOT’s Calculations
Example:
  Meter Point Cap = 600 MW
  Meter Uncertainty = 0.15% (per meter)
  Time Drift = 1% of Interval Length (9 seconds per meter)
  Transformer Uncertainties (N/A as they are shared)
600 x (0.3% + 2%) = 600 x 2.3% = 600 x .023 =
13.8 MW (13800 KW)
For this meter point, the meters can differ +/- 13800 KW and meet all accuracy requirements

## Slide 8: What will the Check Catch?
Hardware/Wiring Errors
  On balance circuit, will catch loss of phase for Energy values down to 41.4 MW (600MW meter point w/13.6MW tolerance)
    Primary = 41.4 MW
    Backup = 27.6 MW
  Bad wiring between CT/PT and meter test switches
  Bad clock circuit in meter resulting in >18 second drift between meters

## Slide 9: What will the Check Catch?
Programming Issues
  Incorrect pulse/energy registration
  Incorrect internal multipliers
  Etc….