## Cover Sheet
ERCOT EPS Site Audit Checklist
This checklist has been developed to facilitate a consistent EPS audit procedure when
validating the compliance of ERCOT EPS meter facilities. Below are some definitions and
explanations regarding the specifics of the audit process.
The checklist has seven category's as listed below:
I. Design Proposal/Facility Details Information
II. Detailed Site Information Check
III. Physical Facility Site Compliance
IV. Instrument Transformer Equipment Standards
V. EPS Meter Specifications
VI. Instrument Circuit Validation Check
VII. Meter Accuracy Test & Load Check Verification
The spreadsheet is designed to capture the results of a field audit upon data entry.
It has multiple rows and columns for data reference and entry.
The document has the Protocol and/or SMOG reference for each item check.
Definitions of the column headers, that utilize a drop down list for data entry, are provided below.
Resource Column-
An auditor will choose from the list of drop downs a selection by which he or she would use
as an aid to performing that specific item check. Depending on the type of check will
dictate which resource will be used.
Check Method-
An auditor will choose the method by which the specific item will be verified. This method
is to be utilized in conjunction with the resource.
How check is confirmed-
Each specific item check is different in the sense that there
could be only one way to confirm the item checked or multiple ways depending on the
uniqueness of that item being checked.
Determination-
This field is checked yes,no,n/a or left blank pending
follow-up information from TDSP

## Comprehensive Audit Process
Site Facility |  | ERCOT EPS Site Audit Form |  |  |  | Date
Design Proposal App. Date |  | Project # | Meter Point |  |  | Auditor |  |  |  |  | Measured Values | Calculations | Visual | TDSP Documentation
Specific Item Check | Protocol Reference | Resource | Check Method | How Confirmed | Determination | Comments |  | MDAS | Equipment Access | TDSP Document | TDSP Engineering Document | Approved EPS Design Proposal | Manufacturer Support Documentation | Approved EPS Design Drawing | Meter Program | EEI Handbook for Metering | Approved EPS Three Line Prints | Test Equipment | Manufacturer Design Specification | Manufacturer Test Documentation | Calculation Sheet | Industry Standard Document | ANSI C57.13 Table 2 | Site Certification Document
Design Proposal/Facility Details Information
Facility Details | Section 10.4.2, paragraph 1, SMOG Technical Metering Attachment B1, item b, c | [8 empty] | Portable Instrument | Indication Instrument | EPS Meter Indication | SCADA
Does One Line accurately reflect the EPS Metering configuration including breakers/by-passes that would affect the metered energy flow? | Section 10.4.2, paragraph 1, SMOG Technical Metering Attachment B1, item b, c, B3, item d | Approved EPS Design Drawing | Visual | Inspected facility electrical connections
Do breakers exist where one line diagram indicates? |  | Approved EPS Design Proposal | Visual | Inspected facility electrical connections |  |  |  | Inspected facility electrical connections
Are CT's located as one line diagram indicates? |  | Approved EPS Design Proposal | Visual | Inspected facility electrical connections
Are VT's located as one line diagram indicates? |  | Approved EPS Design Proposal | Visual | Inspected facility electrical connections
Do three lines and one line drawings match one another? |  | Approved EPS Design Drawing | TDSP Documentation | Reviewed Submitted Prints |  |  |  | Reviewed Submitted Prints
CT Ratio-Does design approved ratio match existing CT ratio? If dual ratio, is the connected ratio correct? |  | Equipment Access | Visual | Perform visual of nameplate |  |  |  | Perform visual of nameplate | Measure primary and secondary | Perform Turns Ratio Test | Measured & Tapped correctly
PT Ratio-Does design approval ratio match existing VT ratio? If dual ratio, is the ratio connected correct? |  | Equipment Access | Visual | Perform visual of nameplate | [5 empty] | Binoculars | De-energized Visual | Photograph | Close Up | Nameplate Visual | Equipment Access
VT Polarity-Are polarity's oriented the correct direction with reference to the design proposal? |  | Equipment Access | Visual | Visually Verified |  |  |  | Visually Verified
CT Polarity-Are polarity's oriented the correct direction with reference to the design proposal? |  | Equipment Access | Visual | Visually Verified | [5 empty] | Yes | No | N/A
Detailed Site Information Check
Netting Scheme-Does physical distance of 400 yards meet protocol? | Section 10.3.2.3, item 4 | TDSP Document | Measured Values | Measured Distance |  |  |  | Measured Distance
MDAS Form (Channel Information) | SMOG Attachment B2, C1
Are EPS meters programmed correctly in reference to Approved Design Proposal? | Attachment B1, item a | Meter Program | Visual | Verified programmed parameters in meter
Channel Assignments-Do IDR programmed channels match the submitted MDAS form? | Attachment C1 | MDAS | Visual | Verified programmed parameters in meter |  |  |  | Verified programmed parameters in meter
Dials-Do number of energy digits match the submitted MDAS form? | Attachment B2, item a (iv) | MDAS | Visual | Verified programmed parameters in meter
UOM-Do device Unit of Measure codes match the submitted MDAS form? | Attachment B2, item a (iv) | MDAS | Visual | Verified programmed parameters in meter
Meter Serial Number, Type & Phone number-Does device serial number, model type and phone number match the submitted MDAS form? | Attachment B2, item a (i) | MDAS | Visual | Verified programmed parameters in meter
Do UOM's, Register ID's & Direction of Flow confirm with MDAS staff? |  | MDAS | Visual | Verified programmed parameters in meter
Multipliers | SMOG Technical Metering Attachment B4, B5, Attachment C9
Do pulse constants verify the IDR pulse multiplier values on the MDAS and pulse calculation sheet? | Attachment B5 | TDSP Document | Calculations | Calculated multipliers using programmed constants |  |  |  | Calculated multipliers using programmed constants | Verify constants, CT & PT ratios
Based on Design Proposal peak load values, does programmed pulse value prevent recorder rollover? | Attachment B5 | TDSP Document | Calculations |  |  |  |  | Visually verified recorder intervals during peak time | Applied maximum current as rated by CT rating and verified pulse count
Do present load conditions satisfy the nominal calculated pulse values with reference to the approved design proposal and load calculations? | Attachment C9 & B5 | TDSP Document | Calculations | Calculated nominal pulses for current condition |  |  |  | Calculated nominal pulses for current condition
Does the IDR generate 25% of maximum pulses for nominal load conditions? | Attachment C9 & B5 | TDSP Document | Calculations | Calculated # of pulses generated based on nominal load |  |  |  | Calculated # of pulses generated based on nominal load | Verified # of pulses from IDR at low peak
Do programmed register constants match the Meter Multiplier calculation sheet? | Attachment B4 | TDSP Document | Calculations | Calculated multipliers using programmed constants
Based on Design Proposal peak load values, does programmed register constant prevent register rollover? | Attachment B4 | TDSP Document | Calculations | Verified rollover calculations |  |  |  | Verified rollover calculations
Do register multiplier values agree with calculation formula? | Attachment B4 | TDSP Document | Calculations | Calculated multipliers using programmed constants
ERCOT Point of Interconnection | Section 10 Protocol
Are EPS meters connected to the ERCOT grid as shown on the Approved Design Proposal? | Section 10.3.2.2 | TDSP Document | Visual | Verified program parameters for energy compensation values |  |  |  | Verified program parameters for energy compensation values
Are EPS meters compensated once and only once if needed? | Section 10.3.2.2 | Meter Program | Visual | Verified loss compensation factors for single point of interconnection |  |  |  | Verified loss compensation factors for single point of interconnection
Meter Program Parameters
Measured Quantities-Are EPS meters programmed for four quadrant measurement? | Exhibit 1, section 3.1, Attachment C1 | Meter Program | Visual | Verified programmed parameters in meter
Event Logging-Does EPS meter have all required events enabled? | Attachment C8, Exhibit 1 section 5.4 | Meter Program | Visual | Verified programmed parameters in meter
Are EPS meters internal energy registers mapped to the proper IDR channels? | Attachment C2 | Meter Program | Visual | Verified actual readings with MDAS assigned channels |  |  |  | Verified actual readings with MDAS assigned channels
Diagnostic Checks-Does EPS meter have required diagnostics enabled? | Exhibit 1, section 5.2 | Meter Program | Visual | Reviewed diagnostics logged in meter, verified all events |  |  |  | Simulated diagnostic event | Reviewed diagnostics logged in meter, verified all events
Transformer Loss Values | SMOG Attachment E2
Does information entered on Loss calculation sheet match the site facility data? | SMOG Attachment E2 | Equipment Access | Visual | Verified site specific equipment for proper data |  |  |  | Verified site specific equipment for proper data
High Voltage Rating-Does voltage rating match manufacturer sheet? |  | Manufacturer Support Documentation | Visual | Visually verified transformer settings |  |  |  | Visually verified transformer settings | Reviewed transformer data sheet
Low Voltage Rating-Does voltage rating match manufacturer sheet? |  | Manufacturer Support Documentation | Visual | Visually verified transformer settings
KVA Rating-Does KVA rating match the Loss compensation sheet? |  | Manufacturer Support Documentation | Visual | Visually verified transformer settings
Are physical high voltage tap settings being used in loss calculations? |  | Equipment Access | Visual | Visually verified transformer settings
Are physical low voltage tap settings being used in loss calculations? | SMOG Attachment E2 | Equipment Access | Visual | Visually verified transformer settings
Transformer Connection-Is transformer connected Wye or Delta? |  | Equipment Access | Visual | Visually verified transformer settings
Transformer Phases-Are there one or three phases? |  | Equipment Access | Visual | Visually verified number of phases |  |  |  | Visually verified number of phases
Meter Elements-Are correct number of elements used in loss calculation? |  | Equipment Access | Visual | Visually verified number of driving elements |  |  |  | Visually verified number of driving elements
Meter Class-Is correct class rating of meter used in loss calculation? |  | Equipment Access | Calculations | Visually verified class rating of meter |  |  |  | Visually verified class rating of meter
Meter Voltage Rating-Is secondary meter voltage used in loss calculation? |  | Equipment Access | Visual | Visually verified voltage rating of meter |  |  |  | Visually verified voltage rating of meter
Percent Impedance-Is nameplate impedance used in loss calculation? |  | Equipment Access | Visual
Percent Excitation-Does excitation match with transformer data sheet? |  | Manufacturer Support Documentation | Visual
No Load Losses
Watt Losses-Does computation of transformer data equal no load watts factor? |  | TDSP Document | Calculations | Calculated data from computer computations |  |  |  | Performed calculations using EEI Handbook for Metering | Calculated data from computer computations
Var Losses-Does computation of transformer data equal no load var factor? |  | TDSP Document | Calculations | Calculated data from computer computations
Full Load Losses | SMOG Attachment E2
Watt Losses-Does computation of transformer data produce no load watt factor? |  | TDSP Document | Calculations | Calculated data from computer computations
Var Losses-Does computation of transformer data produce no load var factor? |  | TDSP Document | Calculations | Calculated data from computer computations
Transformer Load Tap Changer
Is median tap voltage used in loss calculation? |  | Equipment Access | Visual | Visually verified transformer settings
Auto-Transformer Compensation-Are iron and copper losses included in compensation factors? |  | TDSP Document | Visual | Visually verified transformer settings
Line Losses | SMOG Attachment E3
Line Type-What type of line is used in loss calculation? |  |  | TDSP Documentation | Reviewed Engineering data sheet |  |  |  | Reviewed Engineering data sheet
Are correct ohms/mile used in loss computations? |  | Industry Standard Document | TDSP Documentation | Reviewed relay engineering data sheet |  |  |  | Reviewed relay engineering data sheet | Calculated using line design criteria
Line Distance-How many miles of line are used in loss calculation? |  | TDSP Document | Calculations
Do compensation values and registration values agree with ERCOT approved TLC spreadsheet? | Attachment B6 | Site Certification Document | Visual | Verified against ERCOT calculation sheet |  |  |  | Verified against ERCOT calculation sheet
Do EPS meters have correct compensation factors (+ or -) programmed in the meters? |  | Meter Program | Visual | Verified parameters programmed in meters |  |  |  | Verified parameters programmed in meters
Physical Facility Site Compliance
Facility's | SMOG section 5
Does facility environment provide acceptable operating conditions for metering equipment? | SMOG 5.1 (a) | Manufacturer Design Specification | Visual | Visually verified operating environment for EPS equipment |  |  |  | Visually verified operating environment for EPS equipment
Does facility meet the requirement outlined in the NEC, Article 125a? | SMOG 5.1 (b) | Industry Standard Document | Measured Values | Visually verified that space requirements are in compliance with NEC |  |  |  | Visually verified that space requirements are in compliance with NEC
Enclosures-Does EPS metering reside in protected enclosure or structure? | SMOG section 5.2 item a | Equipment Access | Visual | Visually verified enclosure or structure for sound protection |  |  |  | Visually verified enclosure or structure for sound protection
Test Switch Location-Are test switches located at or near the EPS meters? | SMOG section 5.2 | Equipment Access | Visual | Visually verified test switch located near or at meters |  |  |  | Visually verified test switch located near or at meters
Test Switch Functionality-Are test switches wired to allow for removal of a meter without affecting other EPS meters? | SMOG section 5.2 item c | Equipment Access | Visual | Visually verify meter operation |  |  |  | Measured current in opposite test switch | Wire Trace | Visually verify meter operation
Current Shorting Rely Test Block-Is current circuit wired so that during testing there is no disruption to other meters? | SMOG section 5.2 item d | Equipment Access | Visual | Verified IDR data in second meter |  |  |  | Measured current in opposite test switch | Wire Trace | Verified IDR data in second meter
Lighting-Does facility provide adequate lighting? | SMOG section 5.2 item b | Equipment Access | Visual | Performed work detail to satisfaction |  |  |  | Measured illumination levels | Performed work detail to satisfaction
Test Output-Is the electrical test output conveniently accessed? | SMOG section 5.2, paragraph 1 | Equipment Access | Visual | Visually verified accessibility of test output |  |  |  | Visually verified accessibility of test output
Are metering facilitates and secondary devices sealed to protect against unauthorized entry? | Section 10.10.1.5 | Equipment Access | Visual | Visually verified the presence and integrity of sealed devices |  |  |  | Visually verified the presence and integrity of sealed devices
Are existing seals approved ERCOT seals? | Section 10.10.1.5 | Equipment Access | Visual | Visually verified the presence and integrity of sealed devices
Do existing seals match most recent submitted test report? | Section 10.10.1.5 | Equipment Access | Visual | Compare to previous Test Reports |  |  |  | Compare to previous Test Reports
Instrument Transformer Equipment Standards | [6 empty] | Physical Facility Site Compliance | [7 empty] | Physical Facility Site Compliance | [7 empty] | Physical Facility Site Compliance |  | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance
Current Transformers | SMOG Exhibit 2 to Attachment D, section 5.1
BIL Rating-Is CT designed and constructed to ANSI C12.11 or IEEE C57.13-1993 standards? | SMOG Exhibit 2 to Attachment D, section 5.1 | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  |  | Reviewed Manufacturer specification
Winding Configuration-Does CT winding comply with approved typical configurations? | SMOG Exhibit 2 to Attachment D, section 5.3.1,a,b,c,d,e | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  |  | Reviewed Manufacturer specification | Verified Nameplate
Does CT nameplate list the following nameplate items, manufacturer, type of device, serial number, ratios, burden, accuracy class, thermal rating factor, and impulse level? | SMOG Exhibit 2 to Attachment D, section 5.2 | Equipment Access | Visual | Verified Nameplate
Does nameplate data match submitted Site Certification sheet? | SMOG Attachment B, item B3, c | Site Certification Document | Visual | Verified Nameplate
Does nameplate rated primary current (ratio X RF) match approved EPS Design proposal? | SMOG Exhibit 2 to Attachment D, section 5.3.2, Attachment B3, item c | Approved EPS Design Proposal | Visual | Reviewed Manufacturer Certificate of Test |  |  |  | Reviewed Manufacturer specification | Verified Nameplate | Reviewed Manufacturer Certificate of Test
Rated Secondary Current(wire wound)-Is secondary current rated at 5 amps for rated primary amps? | SMOG Exhibit 2 to Attachment D, section 5.3.3 | Manufacturer Test Documentation | Visual | Reviewed Manufacturer specification
Accuracy Class-Is CT designed for minimum standard accuracy of .3 percent? | SMOG Exhibit 2 to Attachment D, section 5.3.5, (a), (b) | Manufacturer Test Documentation | Visual | Reviewed Manufacturer specification
Rated Output(fiber optic)-Is output 1 amp @ rated primary current and used with class 2 meter? | SMOG Exhibit 2 to Attachment D, section 5.3.4 | Equipment Access | Visual | Reviewed Manufacturer specification
Is CL 2 meter being used for Optic CT application? | SMOG Exhibit 1 to Attachment D, section 9.1, item e | Equipment Access | Visual | Reviewed Manufacturer specification
Fiber Optic Accuracy & Burden-Does optic CT meet the standard requirement of .3% accuracy while ensuring the burden is not exceeded? | SMOG Exhibit 2 to Attachment D, section 5.3.6 | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  |  | Reviewed Manufacturer specification | Verified Nameplate | Performed Accuracy Test
Fiber connection is maintained to within manufacturers prescribed limits? | SMOG Exhibit 2 to Attachment D, section 5.3.6 | Manufacturer Design Specification | Visual | Visually verified connection integrity |  |  |  | Visually verified connection integrity
CT Rating Factors-Does CT possess a standard rating factor of 1.0 or higher? | SMOG Exhibit 2 to Attachment D, section 5.3.7, (a), (b) | Manufacturer Test Documentation | Visual | Reviewed Manufacturer specification
Short Time Thermal Current Rating-Does CT meet the requirements for short time thermal currents as prescribed in IEEE 57.13? | SMOG Exhibit 2 to Attachment D, section 5.3.8 | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification
Short Time Mechanical Current Rating-Does CT meet the requirements for short time thermal currents as prescribed in IEEE 57.13? | SMOG Exhibit 2 to Attachment D, section 5.3.9 | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification
Insulating Oil-Has oil been tested for Non-PCB's? | SMOG Exhibit 2 to Attachment D, section 5.6 | Equipment Access | Visual | Reviewed last oil test data |  |  |  | Performed Oil sample test | Reviewed last oil test data
Does Non-PCB nameplate exist on transformer? | SMOG Exhibit 2 to Attachment D, section 5.6 | Equipment Access | Visual | Visually verified nameplate |  |  |  | Visually verified nameplate
Voltage Transformers | SMOG Exhibit 2 section 5.4
Rated Secondary Voltage-Is secondary output of VT rated at 115/69 volts? | SMOG Exhibit 2 section 5.4.3 | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification
Accuracy Class-Is VT designed for minimum standard accuracy of .3 percent? | SMOG Exhibit 2 section 5.4.4 | Manufacturer Test Documentation | Visual | Reviewed Manufacturer specification
Thermal Burden Rating-Does VT meet the IEEE C57.13 requirement for thermal burden? | SMOG Exhibit 2 section 5.4.5 | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  |  | Reviewed Manufacturer specification
Insulating Oil-Has oil been tested for Non-PCB's? | SMOG Exhibit 2 to Attachment D, section 5.6 | Equipment Access | Visual | Reviewed last oil test data
Does Non-PCB nameplate exist on transformer? | SMOG Exhibit 2 to Attachment D, section 5.6 | Equipment Access | Visual | Visually verified nameplate
Instrument Circuit Validation | [6 empty] | Physical Facility Site Compliance | [7 empty] | Physical Facility Site Compliance | [7 empty] | Physical Facility Site Compliance |  | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance
Do test switches permanent or removable allow for the measurement of metered quantities and the application of test values? | SMOG section 2.3 | Equipment Access | Visual | Accessed test switch and measured values |  |  |  | Accessed test switch and measured values | Visually verified operation of meters
Current Transformers | SMOG section 3
Fault Withstand-Does existing CT possess ability to withstand available fault current? | SMOG section 3.1 | TDSP Document | Visual | Reviewed Manufacturer test data |  |  |  | Reviewed Manufacturer test data | TDSP calculated fault current is within limits
CT Quantity | SMOG section 3.2
4-Wire Wye-Do three CT's exist? | SMOG section 3.2 | Equipment Access | Visual | Visually verified # of CT's |  |  |  | Visually verified # of CT's
3-Wire Delta-Do two CT's exist? |  | Equipment Access | Visual | Visually verified # of CT's
Burden | SMOG section 3.3
Is circuit limited to highly accurate billing meters and load control transducers only? | SMOG section 3.3 item a | TDSP Engineering Document | Visual | Wire Trace |  |  |  | Wire Trace | Schematic | Short CT's & Measure Current
Are separate isolated secondaries existing between EPS metering and other allowable meter devices? | SMOG section 3.3 item d | TDSP Engineering Document | Visual | Wire Trace |  |  |  | Wire Trace | Short CT's and Measure Current | Verified test switches or shorting block in circuit
Is the total burden of the CT within the CT Burden Rating? | SMOG section 3.3 item e | Equipment Access | Measured Values | Voltage Drop Test using real load |  |  |  | Voltage Drop Test using real load | Shoot Current & Measure Voltage Drop | Measure ohms of all devices | Reviewed TDSP calculations
Annual Burden Test-Demonstrated connected burden check? | SMOG section 3.3 item f | Equipment Access | Measured Values | Applied burden |  |  |  | Applied burden
Secondary Wiring | SMOG section 3.4
There are no splices in the CT Secondary Wiring? | SMOG section 3.4 item b | Equipment Access | Visual | Wire Trace |  |  |  | Wire Trace
Is wire of sound electrical and mechanical integrity? | SMOG section 3.4 item c | Equipment Access | Visual | Visually verified integrity of wire |  |  |  | Visually verified integrity of wire
Has wire integrity inspection been performed within the last three years? |  | TDSP Document | Visual
Grounding of CT Circuit | SMOG section 3.5
Polarity Conductor-Does each CT have its own polarity conductor? | SMOG section 3.5, item a | Equipment Access | Visual | Visually verified separate conductors |  |  |  | Visually verified separate conductors
Return Conductor-Does each set of CT's have one common return conductor? | SMOG section 3.5, item b | Equipment Access | Visual | Visually verified common return conductor |  |  |  | Visually verified common return conductor
Grounding Point-Is there only one grounded point of the common circuit? | SMOG section 3.5, item c | Equipment Access | Visual | Visually verified one common ground |  |  |  | Visually verified one common ground
Ground wire size-Is the ground conductor of the same size as the polarity and common wire? | SMOG section 3.5, item e | Equipment Access | Visual | Visually verified size of ground wire |  |  |  | Visually verified size of ground wire
Induced Voltages | SMOG section 3.6
Cable Routing-Are cables routed so as to minimize induced voltage effects? | SMOG section 3.6 item a | Equipment Access | Visual | Cable Trace |  |  |  | Cable Trace | Voltage Transient Monitoring
Cable Protection-Is suitable protection available that meets Meter Handbook 10th Edition Chapter 11 pg 352? | SMOG section 3.6 item c | TDSP Document | Visual | Verified protective device to meet Meter Handbook 10th Edition Chapter 11 pg 352 |  |  |  | Verified protective device to meet Meter Handbook 10th Edition Chapter 11 pg 352
Paralleling of CT's | SMOG section 3.7
Nominal Rating-Do all CT's have the same ratio? | SMOG section 3.7, item a | Equipment Access | Visual | Visually verified nameplate |  |  |  | Visually verified nameplate | Verified CT certificate of test
Phase Connection-Are paralleled CT's connected to the same phases? | SMOG section 3.7, item b | Equipment Access | Visual | Visually verified CT's connected to common phase |  |  |  | Visually verified CT's connected to common phase | Measure vectors and calculate algebraic summations
Secondary connections-Do secondary circuits allow for testing of individual CT's? | SMOG section 3.7, item c | Equipment Access | Visual | Independent Test Switches in Circuit |  |  |  | Independent Test Switches in Circuit | Measured current in each test switch
Are CT's paralleled at the meter test switch? | SMOG section 3.7, item c | Equipment Access | Visual | Visually verified circuits are paralleled at meter test switch |  |  |  | Visually verified circuits are paralleled at meter test switch
Grounding Point-Is there only one grounded point for the paralleled CT secondaries? | SMOG section 3.7, item d | Equipment Access | Visual | Visually verified one common ground point |  |  |  | Visually verified one common ground point
Burden Rating-Does each CT possess the ability to support n times the burden within the accuracy class? | SMOG section 3.7, item e | Equipment Access | Visual | Verified calculations |  |  |  | Performed accuracy test at n times the burden | Verified calculations
Common Voltage-Do circuits that have paralleled CT's share a common bus that is normally closed? | SMOG section 3.7, item f | Equipment Access | Visual | Visually verified normally closed bus |  |  |  | Visually verified normally closed bus
Is class rating of meter adequate to measure summation of paralleled currents? | SMOG section 3.7, item g | Equipment Access | Visual | Verified Manufacturer maximum current capacity |  |  |  | Measured total paralleled currents in meter at peak load | Verified Manufacturer maximum current capacity
Sizing Current Transformers | SMOG section 3.8
Is CT sized for optimum metering accuracy at peak and minimum loads? | SMOG section 3.8 | MDAS | Calculations | Verified calculations for max and nominal conditions |  |  |  | Measured secondary current at peak conditions | Measured current at minimum load conditions | Verified calculations for max and nominal conditions
VT Transformers | SMOG section 4
VT Quantity | SMOG section 4.1
Are there three, phase to ground voltages for 4-wire wye sites? | SMOG section 4.1, item a | Equipment Access | Visual |  |  |  |  | Measured magnitudes and angles for three voltages | Wire Trace
Are there three phase to phase voltages for 3-wire delta sites? | SMOG section 4.1, item b | Equipment Access | Visual
Calibration Connections-Does attachment exist for the use of calibration unit for each phase? | SMOG section 4.1 item d | Equipment Access | Visual |  |  |  |  | Visually verified attachment device for each phase
Burden-Is the total VA burden within nameplate rating for each instrument transformer? | SMOG section 4.2 | TDSP Document | Calculations | Measured secondary volt and amps for each phase |  |  |  | Measured secondary volt and amps for each phase
Protection-Are fuses of high speed type? | SMOG section 4.3 | [6 empty] | Simulated high fault condition, measured performance of fuse | Reviewed Manufacturer specifications
Fuses are not installed in the common return or ground circuit? | SMOG section 4.3 | Equipment Access | Visual | Wire Trace |  |  |  | Wire Trace
VT Secondary Wiring | SMOG section 4.4
Voltage Drop-Is there .3 volt drop or less on secondary? | SMOG section 4.4, item a | Test Equipment | Measured Values | Measured voltage drop using multimeter |  |  |  | Measured voltage drop using multimeter
Wire Integrity-Is wire of sound electrical and mechanical integrity? | SMOG section 4.4, item a | Equipment Access | Visual | Visually verified integrity of wire
Has wire integrity inspection been performed within the last three years? |  | TDSP Document | TDSP Documentation | Visually verified integrity of wire
There are no splices in the VT Secondary Wiring? | SMOG section 4.4, item c | Equipment Access | Visual | Wire Trace
Grounding of VT Circuit-Is there only one ground for the set of secondary windings? | SMOG section 4.5 | Equipment Access | Visual | Visually verified one common ground
Induced Voltages | SMOG section 4.6
Cable Routing-Are cables routed so as to minimize induced voltage effects? | SMOG section 4.6 | Equipment Access | Visual | Cable Trace
Cable Protection-Is suitable protection available to protect against faults and switching generated voltages? | SMOG section 4.6 | TDSP Document | Visual
Loss of Potential-Is secondary being monitored for loss of potential for each phase? | SMOG section 4.7 | Equipment Access | Visual | Initiated loss of voltage and verified monitoring function |  |  |  | Verified Meter Program Parameters | Initiated loss of voltage and verified monitoring function
Meter Accuracy Test & Load Check Verification | [6 empty] | Instrument Circuit Validation | [7 empty] | Instrument Circuit Validation | [7 empty] | Instrument Circuit Validation |  | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation
Test Equipment-Are watthour and varhour standards equal to or better than the accuracy of EPS meters? | SMOG section 6.1 | Manufacturer Design Specification | TDSP Documentation | Reviewed Manufacturer's specification sheet |  |  |  | Verified accuracy is equal or better than EPS device | Reviewed Manufacturer's specification sheet
Standard Certification-Have watthour and varhour standards been tested within the last 120 days? | SMOG section 6.2 | TDSP Document | TDSP Documentation | Reviewed Test Standard Certificate of test |  |  |  | Reviewed Test Standard Certificate of test
Correction Factors-Do correction factors exist for test standards and are they retained with standards? | SMOG section 6.2 | TDSP Document | TDSP Documentation | Reviewed correction factors for test standards |  |  |  | Reviewed correction factors for test standards
Calibration Tolerance | SMOG section 6.5
As Found Test-If available are standard pulses and meter pulses recorded on test report? | SMOG section 6.5 | Test Equipment | Visual | Pulse values recorded on test report |  |  |  | Pulse values recorded on test report
Are proper test amps and power factors applied for KWH test? | SMOG section 6.5 | Test Equipment | Visual | Observed proper test point set parameters |  |  |  | Observed proper test point set parameters | Improper test point parameters
If available do generated standard pulses agree with meter pulse counts? |  | Test Equipment | Visual | Calculated expected pulses against input meter pulses |  |  |  | Calculated expected pulses against input meter pulses
Are KWH functions within allotted accuracy tolerance? |  | Site Certification Document | Visual | Verified tolerance levels to be acceptable |  |  |  | Verified tolerance levels to be acceptable | Verified tolerance levels out of tolerance
Are proper test amps and power factors applied for KVARH test? |  | Test Equipment | Visual | Observed proper test point set parameters |  |  |  | Observed proper test point set parameters | Improper test point parameters
If available do generated standard pulses agree with meter pulse counts? |  | Test Equipment | Visual | Calculated expected pulses against input meter pulses |  |  |  | Calculated expected pulses against input meter pulses
Are KVARH functions within allotted accuracy tolerance? | SMOG section 6.5 | Site Certification Document | Visual | Verified tolerance levels to be acceptable |  |  |  | Verified tolerance levels to be acceptable | Verified tolerance levels out of tolerance
Meter Outputs-If outputs sent to an external recorder are used for settlement are they tested and verified for accuracy? | SMOG section 6.6 | TDSP Document | Visual | Verified outputs for settlement are tested for accuracy |  |  |  | Verified outputs for settlement are tested for accuracy
Test Records- Are test records available for last six years? | SMOG section 7.2 | TDSP Document | Visual | Verified archived test data for EPS sites |  |  |  | Verified archived test data for EPS sites
Test Data-Is test data recorded on approved ERCOT Meter Test Report? | SMOG section 8.1, item c | Site Certification Document | Visual | Verified data exist on ERCOT approved Test Report |  |  |  | Verified data exist on ERCOT approved Test Report
Summary Notes | [6 empty] | Meter Accuracy Test & Load Check Verification | [7 empty] | Meter Accuracy Test & Load Check Verification | [7 empty] | Meter Accuracy Test & Load Check Verification |  | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification
Note on A6: This check is a visual check against the ERCOT approved one line detailed drawing, by which the EPS metering would physically match the design schematic. It requires a field inspection to validate the specific items checked. Equipment location shall be verified.
Note on A18: This check is to verify the proper IDR channel assignments/unit of measures, register ID's, serial numbers, and dial configurations. The Channel information section is in reference to the subsection.
Note on A25: This item check validates the calculation formulas used to determine the meter Ke pulse weight for energy pulses. This check will be verified through calculation validations. Maximum load pulses shall be verified as well as minimum pulse for nominal load flow. Register multiplier values are also verified for proper roll over performance requirements.
Note on A36: This check validates that the meter is configured to protocol standards pertaining to channel assignments, measured quantities, diagnostics, event logging, communication parameters, constants and compensation values, recorder parameters, passwords and specific site requirements. This check is performed by extracting text file from the meter showing these parameters.
Note on A41: Verify Transformer loss values by method of visual verification of transformer nameplate data and manufacturer data. Specific items are listed below to be checked. Verify loss compensation factors being used for active and reactive energy.
Note on A55: Verify no load loss calculations for watts and vars with reference to the EEI Handbook for Electricity Metering. Auditor shall assure proper calculations using transformer test data information and meter information.
Note on A58: Verify load loss calculations for watts and vars with reference to the EEI Handbook for Electricity Metering. Auditor shall assure proper calculations using transformer test data information and meter information.
Note on A85: This check is performed to assure that the transformers meet the standards in the ANSI C12.11 or IEEE C57.13-1993 Table 2.
Note on A102: This check is performed to assure that the transformers meet the standards in the ANSI C12.11 or IEEE C57.13-1993 Table 2.

## Option Pick List
| Resource |  | How Confirmed
1 | MDAS | 41 | Visually verified that space requirements are in compliance with NEC
2 | Equipment Access | 42 | Visually verified enclosure or structure for sound protection
3 | TDSP Document | 43 | Visually verified test switch located near or at meters
4 | TDSP Engineering Document | 44 | Measured current in opposite test switch
5 | Approved EPS Design Proposal | 45 | Wire Trace
6 | Manufacturer Support Documentation | 46 | Visually verify meter operation
7 | Approved EPS Design Drawing | 47 | Measured illumination levels
8 | Meter Program | 48 | Performed work detail to satisfaction
9 | EEI Handbook for Metering | 49 | Visually verified accessibility of test output
10 | Approved EPS Three Line Prints | 50 | Visually verified the presence and integrity of sealed devices
11 | Test Equipment | 51 | Compare to previous Test Reports
12 | Manufacturer Design Specification | 52 | Reviewed Manufacturer specification
13 | Manufacturer Test Documentation | 53 | Verified Nameplate
14 | Calculation Sheet | 54 | Reviewed Manufacturer Certificate of Test
15 | Industry Standard Document | 55 | Visually verified connection integrity
16 | ANSI C57.13 Table 2 | 56 | Performed Oil sample test
17 | Site Certification Document | 57 | Reviewed last oil test data
|  | 58 | Performed Accuracy Test
| Compliant | 59 | Visually verified nameplate
1 | Yes | 60 | Reviewed Manufacturer Certificate of Test
2 | No | 61 | Accessed test switch and measured values
|  | 62 | Visually verified operation of meters
| Check Method | 63 | Reviewed Manufacturer test data
1 | Measured Values | 64 | TDSP calculated fault current is within limits
2 | Calculations | 65 | Visually verified # of CT's
3 | Visual | 66 | Wire Trace
4 | TDSP Documentation | 67 | Schematic
|  | 68 | Short CT's & Measure Current
| How Confirmed | 69 | Wire Trace
1 | Inspected facility electrical connections | 70 | Short CT's and Measure Current
2 | Reviewed Submitted Prints | 71 | Verified test switches or shorting block in circuit
3 | Perform visual of nameplate | 72 | Voltage Drop Test using real load
4 | Measure primary and secondary | 73 | Shoot Current & Measure Voltage Drop
5 | Perform Turns Ratio Test | 74 | Measure ohms of all devices
6 | Measured & Tapped correctly | 75 | Reviewed TDSP calculations
7 | Visually Verified | 76 | Applied burden
8 | Measured Distance | 77 | Visually verified integrity of wire
How Confirmed
9 | Verified programmed parameters in meter | 78 | Visually verified separate conductors
10 | Calculated multipliers using programmed constants | 79 | Visually verified common return conductor
11 | Verify constants, CT & PT ratios | 80 | Visually verified one common ground
12 | Visually verified recorder intervals during peak time | 81 | Visually verified size of ground wire
13 | Applied maximum current as rated by CT rating and verified pulse count | 82 | Cable Trace
14 | Calculated nominal pulses for current condition | 83 | Voltage Transient Monitoring
15 | Calculated # of pulses generated based on nominal load | 84 | Verified protective device to meet ANSI C37.90a
16 | Verified # of pulses from IDR at low peak | 85 | Injected fault and measured performance of protective device to C37.90a
17 | Calculated multipliers using programmed constants | 86 | Verified CT certificate of test
18 | Verify constants, CT & PT ratios | 87 | Visually verified CT's connected to common phase
19 | Verified rollover calculations | 88 | Measure vectors and calculate algebraic summations
20 | Verified program parameters for energy compensation values | 89 | Independent Test Switches in Circuit
21 | Verified loss compensation factors for single point of interconnection | 90 | Measured current in each test switch
22 | Verified programmed parameters in meter | 91 | Visually verified circuits are paralleled at meter test switch
23 | Verified actual readings with MDAS assigned channels | 92 | Performed accuracy test at n times the burden
24 | Simulated diagnostic event
25 | Reviewed diagnostics logged in meter, verified all events
26 | Verified site specific equipment for proper data
27 | Visually verified transformer settings
28 | Reviewed transformer data sheet
29 | Visually verified number of phases
30 | Visually verified number of driving elements
31 | Visually verified class rating of meter
32 | Visually verified voltage rating of meter
33 | Performed calculations using EEI Handbook for Metering
34 | Calculated data from computer computations
35 | Reviewed Engineering data sheet
36 | Reviewed relay engineering data sheet
37 | Calculated using line design criteria
38 | Verified against ERCOT calculation sheet
39 | Verified parameters programmed in meters
40 | Visually verified operating environment for EPS equipment

## Blank Comp. Audit Process
Site Facility |  | ERCOT EPS Site Audit Form |  |  |  | Date
Design Proposal App. Date |  | Project # | Meter Point |  |  | Auditor |  |  |  |  | Measured Values | Calculations | Visual | TDSP Documentation
Specific Item Check | Protocol Reference | Resource | Check Method | How Confirmed | Determination | Comments |  | MDAS | Equipment Access | TDSP Document | TDSP Engineering Document | Approved EPS Design Proposal | Manufacturer Support Documentation | Approved EPS Design Drawing | Meter Program | EEI Handbook for Metering | Approved EPS Three Line Prints | Test Equipment | Manufacturer Design Specification | Manufacturer Test Documentation | Calculation Sheet | Industry Standard Document | ANSI C57.13 Table 2 | Site Certification Document
Design Proposal/Facility Details Information
Facility Details | Section 10.4.2, paragraph 1, SMOG Technical Metering Attachment B1, item b, c | [8 empty] | Portable Instrument | Indication Instrument | EPS Meter Indication | SCADA
Does One Line accurately reflect the EPS Metering configuration including breakers/by-passes that would affect the metered energy flow? | Section 10.4.2, paragraph 1, SMOG Technical Metering Attachment B1, item b, c, B3, item d
Do breakers exist where one line diagram indicates? | [7 empty] | Inspected facility electrical connections
Are CT's located as one line diagram indicates?
Are VT's located as one line diagram indicates?
Do three lines and one line drawings match one another? | [7 empty] | Reviewed Submitted Prints
CT Ratio-Does design approved ratio match existing CT ratio? If dual ratio, is the connected ratio correct? | [7 empty] | Perform visual of nameplate | Measure primary and secondary | Perform Turns Ratio Test | Measured & Tapped correctly
PT Ratio-Does design approval ratio match existing VT ratio? If dual ratio, is the ratio connected correct? | [9 empty] | Binoculars | De-energized Visual | Photograph | Close Up | Nameplate Visual | Equipment Access
VT Polarity-Are polarity's oriented the correct direction with reference to the design proposal? | [7 empty] | Visually Verified
CT Polarity-Are polarity's oriented the correct direction with reference to the design proposal? | [9 empty] | Yes | No | N/A
Detailed Site Information Check
Netting Scheme-Does physical distance of 400 yards meet protocol? | Section 10.3.2.3, item 4 | [6 empty] | Measured Distance
MDAS Form (Channel Information) | SMOG Attachment B2, C1
Are EPS meters programmed correctly in reference to Approved Design Proposal? | Attachment B1, item a
Channel Assignments-Do IDR programmed channels match the submitted MDAS form? | Attachment C1 | [6 empty] | Verified programmed parameters in meter
Dials-Do number of energy digits match the submitted MDAS form? | Attachment B2, item a (iv)
UOM-Do device Unit of Measure codes match the submitted MDAS form? | Attachment B2, item a (iv)
Meter Serial Number, Type & Phone number-Does device serial number, model type and phone number match the submitted MDAS form? | Attachment B2, item a (i)
Do UOM's, Register ID's & Direction of Flow confirm with MDAS staff?
Multipliers | SMOG Technical Metering Attachment B4, B5, Attachment C9
Do pulse constants verify the IDR pulse multiplier values on the MDAS and pulse calculation sheet? | Attachment B5 | [6 empty] | Calculated multipliers using programmed constants | Verify constants, CT & PT ratios
Based on Design Proposal peak load values, does programmed pulse value prevent recorder rollover? | Attachment B5 | [6 empty] | Visually verified recorder intervals during peak time | Applied maximum current as rated by CT rating and verified pulse count
Do present load conditions satisfy the nominal calculated pulse values with reference to the approved design proposal and load calculations? | Attachment C9 & B5 | [6 empty] | Calculated nominal pulses for current condition
Does the IDR generate 25% of maximum pulses for nominal load conditions? | Attachment C9 & B5 | [6 empty] | Calculated # of pulses generated based on nominal load | Verified # of pulses from IDR at low peak
Do programmed register constants match the Meter Multiplier calculation sheet? | Attachment B4
Based on Design Proposal peak load values, does programmed register constant prevent register rollover? | Attachment B4 | [6 empty] | Verified rollover calculations
Do register multiplier values agree with calculation formula? | Attachment B4
ERCOT Point of Interconnection | Section 10 Protocol
Are EPS meters connected to the ERCOT grid as shown on the Approved Design Proposal? | Section 10.3.2.2 | [6 empty] | Verified program parameters for energy compensation values
Are EPS meters compensated once and only once if needed? | Section 10.3.2.2 | [6 empty] | Verified loss compensation factors for single point of interconnection
Meter Program Parameters
Measured Quantities-Are EPS meters programmed for four quadrant measurement? | Exhibit 1, section 3.1, Attachment C1
Event Logging-Does EPS meter have all required events enabled? | Attachment C8, Exhibit 1 section 5.4
Are EPS meters internal energy registers mapped to the proper IDR channels? | Attachment C2 | [6 empty] | Verified actual readings with MDAS assigned channels
Diagnostic Checks-Does EPS meter have required diagnostics enabled? | Exhibit 1, section 5.2 | [6 empty] | Simulated diagnostic event | Reviewed diagnostics logged in meter, verified all events
Transformer Loss Values | SMOG Attachment E2
Does information entered on Loss calculation sheet match the site facility data? | SMOG Attachment E2 | [6 empty] | Verified site specific equipment for proper data
High Voltage Rating-Does voltage rating match manufacturer sheet? | [7 empty] | Visually verified transformer settings | Reviewed transformer data sheet
Low Voltage Rating-Does voltage rating match manufacturer sheet?
KVA Rating-Does KVA rating match the Loss compensation sheet?
Are physical high voltage tap settings being used in loss calculations?
Are physical low voltage tap settings being used in loss calculations? | SMOG Attachment E2
Transformer Connection-Is transformer connected Wye or Delta?
Transformer Phases-Are there one or three phases? | [7 empty] | Visually verified number of phases
Meter Elements-Are correct number of elements used in loss calculation? | [7 empty] | Visually verified number of driving elements
Meter Class-Is correct class rating of meter used in loss calculation? | [7 empty] | Visually verified class rating of meter
Meter Voltage Rating-Is secondary meter voltage used in loss calculation? | [7 empty] | Visually verified voltage rating of meter
Percent Impedance-Is nameplate impedance used in loss calculation?
Percent Excitation-Does excitation match with transformer data sheet?
No Load Losses
Watt Losses-Does computation of transformer data equal no load watts factor? | [7 empty] | Performed calculations using EEI Handbook for Metering | Calculated data from computer computations
Var Losses-Does computation of transformer data equal no load var factor?
Full Load Losses | SMOG Attachment E2
Watt Losses-Does computation of transformer data produce no load watt factor?
Var Losses-Does computation of transformer data produce no load var factor?
Transformer Load Tap Changer
Is median tap voltage used in loss calculation?
Auto-Transformer Compensation-Are iron and copper losses included in compensation factors?
Line Losses | SMOG Attachment E3
Line Type-What type of line is used in loss calculation? | [7 empty] | Reviewed Engineering data sheet
Are correct ohms/mile used in loss computations? | [7 empty] | Reviewed relay engineering data sheet | Calculated using line design criteria
Line Distance-How many miles of line are used in loss calculation?
Do compensation values and registration values agree with ERCOT approved TLC spreadsheet? | Attachment B6 | [6 empty] | Verified against ERCOT calculation sheet
Do EPS meters have correct compensation factors (+ or -) programmed in the meters? | [7 empty] | Verified parameters programmed in meters
Physical Facility Site Compliance
Facility's | SMOG section 5
Does facility environment provide acceptable operating conditions for metering equipment? | SMOG 5.1 (a) | [6 empty] | Visually verified operating environment for EPS equipment
Does facility meet the requirement outlined in the NEC, Article 125a? | SMOG 5.1 (b) | [6 empty] | Visually verified that space requirements are in compliance with NEC
Enclosures-Does EPS metering reside in protected enclosure or structure? | SMOG section 5.2 item a | [6 empty] | Visually verified enclosure or structure for sound protection
Test Switch Location-Are test switches located at or near the EPS meters? | SMOG section 5.2 | [6 empty] | Visually verified test switch located near or at meters
Test Switch Functionality-Are test switches wired to allow for removal of a meter without affecting other EPS meters? | SMOG section 5.2 item c | [6 empty] | Measured current in opposite test switch | Wire Trace | Visually verify meter operation
Current Shorting Rely Test Block-Is current circuit wired so that during testing there is no disruption to other meters? | SMOG section 5.2 item d | [6 empty] | Measured current in opposite test switch | Wire Trace | Verified IDR data in second meter
Lighting-Does facility provide adequate lighting? | SMOG section 5.2 item b | [6 empty] | Measured illumination levels | Performed work detail to satisfaction
Test Output-Is the electrical test output conveniently accessed? | SMOG section 5.2, paragraph 1 | [6 empty] | Visually verified accessibility of test output
Are metering facilitates and secondary devices sealed to protect against unauthorized entry? | Section 10.10.1.5 | [6 empty] | Visually verified the presence and integrity of sealed devices
Are existing seals approved ERCOT seals? | Section 10.10.1.5
Do existing seals match most recent submitted test report? | Section 10.10.1.5 | [6 empty] | Compare to previous Test Reports
Instrument Transformer Equipment Standards | [6 empty] | Physical Facility Site Compliance | [7 empty] | Physical Facility Site Compliance | [7 empty] | Physical Facility Site Compliance |  | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance
Current Transformers | SMOG Exhibit 2 to Attachment D, section 5.1
BIL Rating-Is CT designed and constructed to ANSI C12.11 or IEEE C57.13-1993 standards? | SMOG Exhibit 2 to Attachment D, section 5.1 | [6 empty] | Reviewed Manufacturer specification
Winding Configuration-Does CT winding comply with approved typical configurations? | SMOG Exhibit 2 to Attachment D, section 5.3.1,a,b,c,d,e | [6 empty] | Reviewed Manufacturer specification | Verified Nameplate
Does CT nameplate list the following nameplate items, manufacturer, type of device, serial number, ratios, burden, accuracy class, thermal rating factor, and impulse level? | SMOG Exhibit 2 to Attachment D, section 5.2
Does nameplate data match submitted Site Certification sheet? | SMOG Attachment B, item B3, c
Does nameplate rated primary current (ratio X RF) match approved EPS Design proposal? | SMOG Exhibit 2 to Attachment D, section 5.3.2, Attachment B3, item c | [6 empty] | Reviewed Manufacturer specification | Verified Nameplate | Reviewed Manufacturer Certificate of Test
Rated Secondary Current(wire wound)-Is secondary current rated at 5 amps for rated primary amps? | SMOG Exhibit 2 to Attachment D, section 5.3.3
Accuracy Class-Is CT designed for minimum standard accuracy of .3 percent? | SMOG Exhibit 2 to Attachment D, section 5.3.5, (a), (b)
Rated Output(fiber optic)-Is output 1 amp @ rated primary current and used with class 2 meter? | SMOG Exhibit 2 to Attachment D, section 5.3.4
Is CL 2 meter being used for Optic CT application? | SMOG Exhibit 1 to Attachment D, section 9.1, item e
Fiber Optic Accuracy & Burden-Does optic CT meet the standard requirement of .3% accuracy while ensuring the burden is not exceeded? | SMOG Exhibit 2 to Attachment D, section 5.3.6 | [6 empty] | Reviewed Manufacturer specification | Verified Nameplate | Performed Accuracy Test
Fiber connection is maintained to within manufacturers prescribed limits? | SMOG Exhibit 2 to Attachment D, section 5.3.6 | [6 empty] | Visually verified connection integrity
CT Rating Factors-Does CT possess a standard rating factor of 1.0 or higher? | SMOG Exhibit 2 to Attachment D, section 5.3.7, (a), (b)
Short Time Thermal Current Rating-Does CT meet the requirements for short time thermal currents as prescribed in IEEE 57.13? | SMOG Exhibit 2 to Attachment D, section 5.3.8
Short Time Mechanical Current Rating-Does CT meet the requirements for short time thermal currents as prescribed in IEEE 57.13? | SMOG Exhibit 2 to Attachment D, section 5.3.9
Insulating Oil-Has oil been tested for Non-PCB's? | SMOG Exhibit 2 to Attachment D, section 5.6 | [6 empty] | Performed Oil sample test | Reviewed last oil test data
Does Non-PCB nameplate exist on transformer? | SMOG Exhibit 2 to Attachment D, section 5.6 | [6 empty] | Visually verified nameplate
Voltage Transformers | SMOG Exhibit 2 section 5.4
Rated Secondary Voltage-Is secondary output of VT rated at 115/69 volts? | SMOG Exhibit 2 section 5.4.3
Accuracy Class-Is VT designed for minimum standard accuracy of .3 percent? | SMOG Exhibit 2 section 5.4.4
Thermal Burden Rating-Does VT meet the IEEE C57.13 requirement for thermal burden? | SMOG Exhibit 2 section 5.4.5 | [6 empty] | Reviewed Manufacturer specification
Insulating Oil-Has oil been tested for Non-PCB's? | SMOG Exhibit 2 to Attachment D, section 5.6
Does Non-PCB nameplate exist on transformer? | SMOG Exhibit 2 to Attachment D, section 5.6
Instrument Circuit Validation | [6 empty] | Physical Facility Site Compliance | [7 empty] | Physical Facility Site Compliance | [7 empty] | Physical Facility Site Compliance |  | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance | Physical Facility Site Compliance
Do test switches permanent or removable allow for the measurement of metered quantities and the application of test values? | SMOG section 2.3 | [6 empty] | Accessed test switch and measured values | Visually verified operation of meters
Current Transformers | SMOG section 3
Fault Withstand-Does existing CT possess ability to withstand available fault current? | SMOG section 3.1 | [6 empty] | Reviewed Manufacturer test data | TDSP calculated fault current is within limits
CT Quantity | SMOG section 3.2
4-Wire Wye-Do three CT's exist? | SMOG section 3.2 | [6 empty] | Visually verified # of CT's
3-Wire Delta-Do two CT's exist?
Burden | SMOG section 3.3
Is circuit limited to highly accurate billing meters and load control transducers only? | SMOG section 3.3 item a | [6 empty] | Wire Trace | Schematic | Short CT's & Measure Current
Are separate isolated secondaries existing between EPS metering and other allowable meter devices? | SMOG section 3.3 item d | [6 empty] | Wire Trace | Short CT's and Measure Current | Verified test switches or shorting block in circuit
Is the total burden of the CT within the CT Burden Rating? | SMOG section 3.3 item e | [6 empty] | Voltage Drop Test using real load | Shoot Current & Measure Voltage Drop | Measure ohms of all devices | Reviewed TDSP calculations
Annual Burden Test-Demonstrated connected burden check? | SMOG section 3.3 item f | [6 empty] | Applied burden
Secondary Wiring | SMOG section 3.4
There are no splices in the CT Secondary Wiring? | SMOG section 3.4 item b | [6 empty] | Wire Trace
Is wire of sound electrical and mechanical integrity? | SMOG section 3.4 item c | [6 empty] | Visually verified integrity of wire
Has wire integrity inspection been performed within the last three years?
Grounding of CT Circuit | SMOG section 3.5
Polarity Conductor-Does each CT have its own polarity conductor? | SMOG section 3.5, item a | [6 empty] | Visually verified separate conductors
Return Conductor-Does each set of CT's have one common return conductor? | SMOG section 3.5, item b | [6 empty] | Visually verified common return conductor
Grounding Point-Is there only one grounded point of the common circuit? | SMOG section 3.5, item c | [6 empty] | Visually verified one common ground
Ground wire size-Is the ground conductor of the same size as the polarity and common wire? | SMOG section 3.5, item e | [6 empty] | Visually verified size of ground wire
Induced Voltages | SMOG section 3.6
Cable Routing-Are cables routed so as to minimize induced voltage effects? | SMOG section 3.6 item a | [6 empty] | Cable Trace | Voltage Transient Monitoring
Cable Protection-Is suitable protection available that meets Meter Handbook 10th Edition Chapter 11 pg 352? | SMOG section 3.6 item c | [6 empty] | Cable Protection-Is suitable protection available that meets Meter Handbook 10th Edition Chapter 11 pg 352?
Paralleling of CT's | SMOG section 3.7
Nominal Rating-Do all CT's have the same ratio? | SMOG section 3.7, item a | [6 empty] | Visually verified nameplate | Verified CT certificate of test
Phase Connection-Are paralleled CT's connected to the same phases? | SMOG section 3.7, item b | [6 empty] | Visually verified CT's connected to common phase | Measure vectors and calculate algebraic summations
Secondary connections-Do secondary circuits allow for testing of individual CT's? | SMOG section 3.7, item c | [6 empty] | Independent Test Switches in Circuit | Measured current in each test switch
Are CT's paralleled at the meter test switch? | SMOG section 3.7, item c | [6 empty] | Visually verified circuits are paralleled at meter test switch
Grounding Point-Is there only one grounded point for the paralleled CT secondaries? | SMOG section 3.7, item d | [6 empty] | Visually verified one common ground point
Burden Rating-Does each CT possess the ability to support n times the burden within the accuracy class? | SMOG section 3.7, item e | [6 empty] | Performed accuracy test at n times the burden | Verified calculations
Common Voltage-Do circuits that have paralleled CT's share a common bus that is normally closed? | SMOG section 3.7, item f | [6 empty] | Visually verified normally closed bus
Is class rating of meter adequate to measure summation of paralleled currents? | SMOG section 3.7, item g | [6 empty] | Measured total paralleled currents in meter at peak load | Verified Manufacturer maximum current capacity
Sizing Current Transformers | SMOG section 3.8
Is CT sized for optimum metering accuracy at peak and minimum loads? | SMOG section 3.8 | [6 empty] | Measured secondary current at peak conditions | Measured current at minimum load conditions | Verified calculations for max and nominal conditions
VT Transformers | SMOG section 4
VT Quantity | SMOG section 4.1
Are there three, phase to ground voltages for 4-wire wye sites? | SMOG section 4.1, item a | [6 empty] | Measured magnitudes and angles for three voltages | Wire Trace
Are there three phase to phase voltages for 3-wire delta sites? | SMOG section 4.1, item b
Calibration Connections-Does attachment exist for the use of calibration unit for each phase? | SMOG section 4.1 item d | [6 empty] | Visually verified attachment device for each phase
Burden-Is the total VA burden within nameplate rating for each instrument transformer? | SMOG section 4.2 | [6 empty] | Measured secondary volt and amps for each phase
Protection-Are fuses of high speed type? | SMOG section 4.3 | [6 empty] | Simulated high fault condition, measured performance of fuse | Reviewed Manufacturer specifications
Fuses are not installed in the common return or ground circuit? | SMOG section 4.3 | [6 empty] | Wire Trace
VT Secondary Wiring | SMOG section 4.4
Voltage Drop-Is there .3 volt drop or less on secondary? | SMOG section 4.4, item a | [6 empty] | Measured voltage drop using multimeter
Wire Integrity-Is wire of sound electrical and mechanical integrity? | SMOG section 4.4, item a
Has wire integrity inspection been performed within the last three years?
There are no splices in the VT Secondary Wiring? | SMOG section 4.4, item c
Grounding of VT Circuit-Is there only one ground for the set of secondary windings? | SMOG section 4.5
Induced Voltages | SMOG section 4.6
Cable Routing-Are cables routed so as to minimize induced voltage effects? | SMOG section 4.6
Cable Protection-Is suitable protection available to protect against faults and switching generated voltages? | SMOG section 4.6
Loss of Potential-Is secondary being monitored for loss of potential for each phase? | SMOG section 4.7 | [6 empty] | Verified Meter Program Parameters | Initiated loss of voltage and verified monitoring function
Meter Accuracy Test & Load Check Verification | [6 empty] | Instrument Circuit Validation | [7 empty] | Instrument Circuit Validation | [7 empty] | Instrument Circuit Validation |  | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation
Test Equipment-Are watthour and varhour standards equal to or better than the accuracy of EPS meters? | SMOG section 6.1 | [6 empty] | Verified accuracy is equal or better than EPS device | Reviewed Manufacturer's specification sheet
Standard Certification-Have watthour and varhour standards been tested within the last 120 days? | SMOG section 6.2 | [6 empty] | Reviewed Test Standard Certificate of test
Correction Factors-Do correction factors exist for test standards and are they retained with standards? | SMOG section 6.2 | [6 empty] | Reviewed correction factors for test standards
Calibration Tolerance | SMOG section 6.5
As Found Test-If available are standard pulses and meter pulses recorded on test report? | SMOG section 6.5 | [6 empty] | Pulse values recorded on test report
Are proper test amps and power factors applied for KWH test? | SMOG section 6.5 | [6 empty] | Observed proper test point set parameters | Improper test point parameters
If available do generated standard pulses agree with meter pulse counts? | [7 empty] | Calculated expected pulses against input meter pulses
Are KWH functions within allotted accuracy tolerance? | [7 empty] | Verified tolerance levels to be acceptable | Verified tolerance levels out of tolerance
Are proper test amps and power factors applied for KVARH test? | [7 empty] | Observed proper test point set parameters | Improper test point parameters
If available do generated standard pulses agree with meter pulse counts? | [7 empty] | Calculated expected pulses against input meter pulses
Are KVARH functions within allotted accuracy tolerance? | SMOG section 6.5 | [6 empty] | Verified tolerance levels to be acceptable | Verified tolerance levels out of tolerance
Meter Outputs-If outputs sent to an external recorder are used for settlement are they tested and verified for accuracy? | SMOG section 6.6 | [6 empty] | Verified outputs for settlement are tested for accuracy
Test Records- Are test records available for last six years? | SMOG section 7.2 | [6 empty] | Verified archived test data for EPS sites
Test Data-Is test data recorded on approved ERCOT Meter Test Report? | SMOG section 8.1, item c | [6 empty] | Verified data exist on ERCOT approved Test Report
Summary Notes | [6 empty] | Meter Accuracy Test & Load Check Verification | [7 empty] | Meter Accuracy Test & Load Check Verification | [7 empty] | Meter Accuracy Test & Load Check Verification |  | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification | Meter Accuracy Test & Load Check Verification
Note on A6: This check is a visual check against the ERCOT approved one line detailed drawing, by which the EPS metering would physically match the design schematic. It requires a field inspection to validate the specific items checked. Equipment location shall be verified.
Note on A18: This check is to verify the proper IDR channel assignments/unit of measures, register ID's, serial numbers, and dial configurations. The Channel information section is in reference to the subsection.
Note on A25: This item check validates the calculation formulas used to determine the meter Ke pulse weight for energy pulses. This check will be verified through calculation validations. Maximum load pulses shall be verified as well as minimum pulse for nominal load flow. Register multiplier values are also verified for proper roll over performance requirements.
Note on A36: This check validates that the meter is configured to protocol standards pertaining to channel assignments, measured quantities, diagnostics, event logging, communication parameters, constants and compensation values, recorder parameters, passwords and specific site requirements. This check is performed by extracting text file from the meter showing these parameters.
Note on A41: Verify Transformer loss values by method of visual verification of transformer nameplate data and manufacturer data. Specific items are listed below to be checked. Verify loss compensation factors being used for active and reactive energy.
Note on A55: Verify no load loss calculations for watts and vars with reference to the EEI Handbook for Electricity Metering. Auditor shall assure proper calculations using transformer test data information and meter information.
Note on A58: Verify load loss calculations for watts and vars with reference to the EEI Handbook for Electricity Metering. Auditor shall assure proper calculations using transformer test data information and meter information.
Note on A85: This check is performed to assure that the transformers meet the standards in the ANSI C12.11 or IEEE C57.13-1993 Table 2.
Note on A102: This check is performed to assure that the transformers meet the standards in the ANSI C12.11 or IEEE C57.13-1993 Table 2.

## Three VT-Two CT Applications
Site Facility |  | ERCOT EPS Site Audit Form Three VT-Two CT Application |  |  |  | Date
Design Proposal App. Date |  | Project # | Meter Point |  |  | Auditor |  |  |  | Measured Values | Calculations | Visual | TDSP Documentation
Specific Item Check | Protocol Reference | Resource | Check Method | How Confirmed | Determination | Comments | MDAS | Equipment Access | TDSP Document | TDSP Engineering Document | Approved EPS Design Proposal | Manufacturer Support Documentation | Approved EPS Design Drawing | Meter Program | EEI Handbook for Metering | Approved EPS Three Line Prints | Test Equipment | Manufacturer Design Specification | Manufacturer Test Documentation | Calculation Sheet | Industry Standard Document | ANSI C57.13 Table 2 | Site Certification Document
Instrument Circuit Validation | [6 empty] | Instrument Circuit Validation | [7 empty] | Instrument Circuit Validation | [7 empty] | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation
Current Transformers
Three VT-Two CT Metering | SMOG section 3.2
Are all power transformers primary connections behind the metering point are ungrounded delta, ungrounded wye or phase to phase? |  |  | Visual | Verified transformer connections |  |  | Verified transformer connections
Has the TDSP verified on an annual basis that all power transformers primary connections behind the metering point are ungrounded delta, ungrounded wye or phase to phase? |  |  | Visual | Visually verified no single phase loads |  |  | Visually verified no single phase loads | Perform KVA/KW Load Check
There are no phase-to-ground loads or phase-to-ground sources connected between the metering point and the power transformer primary connections? |  |  | Visual | Visually verified no single phase sources |  |  | Visually verified no single phase sources
One Line Detail-Does one line detail show all tapped power transformers? |  |  | Visual | Visually verified all power transformer connections |  |  | Visually verified all power transformer connections
Voltage Transformers
Three VT-Two CT Metering | SMOG section 4.1, item c
Are VT's connected delta on secondary? | SMOG section 4.1, item c |  | Visual | Visually verified VT connections |  |  | Visually verified VT connections
Are there loads connected that provide path for power to ground? |  |  | Visual
Are the VT's connected to the grounding system of the transmission system? |  |  | Visual | Visually verified ground connection |  |  | Visually verified ground connection
Are meter potentials connected phase to common phase? | SMOG section 4.1, item c |  | Visual | Wire Trace |  |  | Wire Trace
Are secondary of potentials connected the grounding system? |  |  | Visual

## EPS Meter Standards
Site Facility |  | ERCOT EPS Site Audit Form EPS Meters |  |  |  | Date
Design Proposal App. Date |  | Project # | Meter Point |  |  | Auditor |  |  |  | Measured Values | Calculations | Visual | TDSP Documentation
Specific Item Check | Protocol Reference | Resource | Check Method | How Confirmed | Determination | Comments | MDAS | Equipment Access | TDSP Document | TDSP Engineering Document | Approved EPS Design Proposal | Manufacturer Support Documentation | Approved EPS Design Drawing | Meter Program | EEI Handbook for Metering | Approved EPS Three Line Prints | Test Equipment | Manufacturer Design Specification | Manufacturer Test Documentation | Calculation Sheet | Industry Standard Document | ANSI C57.13 Table 2 | Site Certification Document
EPS Meter Specifications | [12 empty] | Instrument Circuit Validation | [7 empty] | Instrument Circuit Validation |  |  | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation | Instrument Circuit Validation
Meter Requirement Specifications | SMOG Exhibit 1 Attachment D sections 1-6
Metered Quantities-Do EPS meters possess the ability to measure true four quadrant measurement? | SMOG Exhibit 1 to Attachment D section 3.1 | Manufacturer Support Documentation | Visual | Reviewed Manufacturer specification |  |  | Reviewed Manufacturer specification | Applied four quadrant load and verified meter's ability |  |  | Yes | No
Kilovars flowing out of ERCOT-Does EPS meter measure var delivered energy in quadrants 1 & 2? | SMOG Exhibit 1 to Attachment D section 3.1, item b | Meter Program | Visual | Applied four quadrant load and verified meter's ability
Kilovars flowing into ERCOT-Does EPS meter measure var delivered energy in quadrants 3 & 4? | SMOG Exhibit 1 to Attachment D section 3.1, item c | Meter Program | Visual | Applied four quadrant load and verified meter's ability
Data Recording Function | SMOG Exhibit 1 to Attachment D section 3.3, item, a, b, d,e,f
Does recorder provide 4 channel recording capability? | SMOG Exhibit 1 to Attachment D section 3.3, item, a | Manufacturer Design Specification | Visual | Visually verified physical number of channels available |  |  | Visually verified physical number of channels available
Are the date and time stored along with the interval data? | SMOG Exhibit 1 to Attachment D section 3.3, item, b | Manufacturer Support Documentation | Visual | Visually verified raw interval data with date and time stamp |  |  | Visually verified raw interval data with date and time stamp
Memory-Does EPS meter have sufficient memory to store 45 days of 4 channel 15 minute interval data? | SMOG Exhibit 1 to Attachment D section 3.3, item, d | TDSP Document | Calculations | Reviewed Manufacturer specification |  |  | Reviewed Manufacturer specification | Programmed 4 channels and verified data capacity
Memory Capacity-Does IDR count and store at least of 4,000 counts in a single interval? | SMOG Exhibit 1 to Attachment D section 3.3, item, e | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  | Reviewed Manufacturer specification | Applied class amps to meter and verified pulse count
Recording During Communications-Does the meter record interval data while communications session is active, through any port? | SMOG Exhibit 1 to Attachment D section 3.3, item, f | Equipment Access | Visual | Applied load and initiated communications to meter |  |  | Reviewed Manufacturer specification | Applied load and initiated communications to meter
Power Disturbance Functionality | SMOG Exhibit 1 to Attachment D section 3.4
Retention of Data-During power outage, does meter maintain all data and time/date marks? | SMOG Exhibit 1 to Attachment D section 3.4, items a | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  | Reviewed Manufacturer specification | Simulated power outage and verified data was present upon power up
Register Catch Up-Does meter register catch up within the 30 second required time after an outage? | SMOG Exhibit 1 to Attachment D section 3.4, items d | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  | Reviewed Manufacturer specification | Applied load and measured time for register catch up
Power Outage-Does meter record the time and date of power outage conditions? | SMOG Exhibit 1 to Attachment D section 3.4, items f | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  | Reviewed Manufacturer specification | Simulated power outage and verified event was logged
Does EPS meter have ability to set the power outage length time to sixty seconds for loss of potential? | Attachment C6 | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  | Reviewed Manufacturer specification | Simulated power outage time less than sixty seconds and verified no event logged
Test Mode Functionality | SMOG Exhibit 1 to Attachment D section 3.5, items a, b, c,
Normal Mode Suspend-During test mode is recording suspended for IDR and normal registers? | SMOG Exhibit 1 to Attachment D section 3.5, items a, | Manufacturer Design Specification | Visual | Initiate test mode and observed absence of data |  |  | Reviewed Manufacturer specification | Initiate test mode and observed absence of data
Test Mode Security-Is meter programmed to limit unauthorized access in test mode? | SMOG Exhibit 1 to Attachment D section 3.5, items b | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  | Reviewed Manufacturer specification | Initiated incorrect password
Test Mode Deactivation-Is meter programmed to exit test mode within one hour or less? | SMOG Exhibit 1 to Attachment D section 3.5, items d | Manufacturer Design Specification | Visual | Reviewed Meter Program |  |  | Reviewed Meter Program | Performed timed test
Meter Display-Does EPS meter meet ANSI C12.1, C12.20, and C12.10 for quantities displayed? | SMOG Exhibit 1 to Attachment D section 4.1 | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  | Reviewed Manufacturer specification
Does meter power up in normal display mode after a power outage? | SMOG Exhibit 1 to Attachment D section 4.1 | Manufacturer Design Specification | Visual | De-energized meter and re-energized and verified display in normal mode |  |  | De-energized meter and re-energized and verified display in normal mode
Compensated Values-For compensated sites, does meter display compensated energy values? | SMOG Exhibit 1 to Attachment D section 4.3 | Manufacturer Design Specification | Visual | Visually verified meter register parameters |  |  | Reviewed Manufacturer specification | Visually verified meter register parameters
Self Test-Does meter perform self test for register functionality per the SMOG requirements? | SMOG Exhibit 1 to Attachment D section 5.1, items a, b, c, | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification
Diagnostic Check-In the event of diagnostic failure, does EPS meter store the event that is retrievable by the MDAS? | SMOG Exhibit 1 to Attachment D section 5.2, items a, b, c, | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification
Does meter report pulse overflow if pulses exceed recorder storage capability? | SMOG Exhibit 1 to Attachment D section 5.3 | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  | Simulated pulse overflow condition and verified flag within interval data
Event Logging-Is meter programmed to log all events as listed in SMOG? | SMOG Exhibit 1 to Attachment D section 5.4 | Manufacturer Design Specification | Visual | Reviewed Meter Program |  |  | Reviewed Meter Program | Simulated event occurrence and verified logging
Local Communications Interface-Does EPS meter possess ability to communicate locally? | SMOG Exhibit 1 to Attachment D section 6.1 | Manufacturer Design Specification | Visual | Communicated locally |  |  | Reviewed Manufacturer specification | Communicated locally
Does modem communicate at a minimum baud rate of 1200 baud? Is modem configurable for answer windows, and ring counters? | SMOG Exhibit 1 to Attachment D section 6.1 | Manufacturer Design Specification | Visual | Verified modem communicates at 1200 baud or higher |  |  | Verified modem communicates at 1200 baud or higher
Accuracy Class | SMOG Exhibit 1 to Attachment D section 8.1
Loads <10MW-Are EPS meters designed to meet ANSI C12.1? | SMOG Exhibit 1 to Attachment D section 8.1 | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  | Reviewed Manufacturer specification
Loads >10MW-Are EPS meters designed to meet ANSI C12.20, 0.2 accuracy class? | SMOG Exhibit 1 to Attachment D section 8.1 | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  | Reviewed Manufacturer specification
Start-up Delay-Does meter begin calculations within 3 seconds of power application? | SMOG Exhibit 1 to Attachment D section 8.3 | Manufacturer Design Specification | Visual | Reviewed Manufacturer specification |  |  | Reviewed Manufacturer specification
Meter Conformance Requirements | SMOG Exhibit 1 to Attachment D section 13.3
TDSP Approved Meters
Firmware-Does documentation exist showing current firmware versions being used by TDSP? | SMOG Exhibit 1 to Attachment D section 13.3 item, 1-a | TDSP Document | Visual | Reviewed TDSP Records for compliance |  |  | Reviewed TDSP Records for compliance
Software-Does documentation exist showing current software versions being used by TDSP? | SMOG Exhibit 1 to Attachment D section 13.3 item, 1-a, b, c, d, e, f | TDSP Document | Visual | Reviewed TDSP Records for compliance
Deployment Date-Document showing date which approved device was entered into service? | SMOG Exhibit 1 to Attachment D section 13.3 item, 1-a, b, c, d, e, f | TDSP Document | Visual | Reviewed TDSP Records for compliance
Certification Letter-Does TDSP possess letter certifying compliance of meter with ANSI/IEC standards and ERCOT Protocols? |  | Manufacturer Support Documentation | Visual | Reviewed TDSP Records for compliance
Test Data-Does TDSP possess document from manufacturer detailing testing certification? | SMOG Exhibit 1 to Attachment D section 13.3 item, 1-a, b, c, d, e, f | Manufacturer Support Documentation | Visual | Reviewed TDSP Records for compliance
Drawings/Technical Manuals-Does TDSP possess necessary schematics and technical manuals for installation and maintenance of device? |  | Manufacturer Support Documentation | Visual | Reviewed TDSP Records for compliance
Note on A5: Meter specifications shall meet or exceed the SMOG requirements for settlement quality data.