| PRR Number | 468PRR | PRR Title | Frequency Response Requirements and Monitoring |
| --- | --- | --- | --- |
| Date |  | 02/16/04 |  |
| Submitter’s Information |  |  |  |
| Name |  | Jeff Gerber |  |
| E-mail Address |  | jgerber@ercot.com |  |
| Company |  | ERCOT |  |
| Company Address |  | 7620 Metro Center Drive, Austin 78744 |  |
| Phone Number |  | 512-225-7033 |  |
| Fax Number |  | 512-225-7165 |  |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

|  | Impact |  | Benefit |
| --- | --- | --- | --- |
|  | Business | Computer Systems |  |
| ERCOT | ERCOT Compliance and Operation would be tasked with monitoring and reporting of performance and ERCOT would reassess annually the amount of governor response required. | No direct impacts to ERCOT systems. | Reliability improvement. |
| MARKET SEGMENT |  |  |  |
| Consumer | Not known. | Not known. | Reliability improvement. |
| LSE: General, Including NOIE | Not known. | Not known. | Reliability improvement. |
| LSE: CR & REP | Not known. | Not known. | Reliability improvement. |
| QSE | Would need to conform with standards on a portfolio-wide basis. | Support for new monitoring and reporting requirements. | Reliability improvement. |
| Resource | Could result in installation and maintenance of frequency response governors, dependent on arrangement with the QSE and ERCOT. | Support for maintenance and testing of frequency response governors where applicable. | Reliability improvement. |
| TDSP | Not known. | Not known. | Reliability improvement. |

Comments

The revision and recommendation of the Frequency Control task force would allow QSEs to meet the 420 MW/0.1 Hz standard on a portfolio basis.  ERCOT supports the Comments submitted by the Chair of the task force as they would benchmark ERCOT’s ability to manage system frequency, and therefore establish a reference to ensure that reliability does not decrease in the future.  ERCOT recommends the following revisions for clarification and conformance to the Protocols, and a revision to Section 5.8.3.1 to show that the data included is available from real-time sources, but not all of the data is available by two (2)–second scans.

Revised Proposed Protocol Language

(The following shall be added to Section 5 of the Protocols)

## 5.8	Frequency Response Requirements and  Monitoring

### 5.8.1	Generation Resource and QSE Participation

#### 5.8.1.1	Governor in Service

At all times a Generation Resource is on line, its turbine governor shall remain in service and be allowed to respond to all changes in system frequency.  Generation Entities shall not reduce governor response on individual Resources during abnormal conditions without ERCOT’s consent (conveyed by way of the Generation Entity’s QSE) unless equipment damage is imminent.

#### 5.8.1.2	Reporting

Generation Entities shall conduct applicable generating governor speed regulation tests on Resources as specified in the Operating Guides.  Test results and/or other relevant information shall be reported to ERCOT and ERCOT shall forward results to the appropriate TSPs.

Resource governor modeling information required in the ERCOT Planning Criteria shall be determined from actual Resource testing described in the Operating Guides.  Within thirty (30) days of ERCOT’s request, the results of the latest test performed shall be supplied to ERCOT and the connected TSP.

When the governor of a Generation Resource is blocked while the Resource is operating, the QSE shall promptly inform ERCOT.  The QSE shall also supply governor status logs to ERCOT upon request.

Any short-term inability of a Generation Resource to supply governor response shall be immediately reported to ERCOT.

If a Generation Resource trips Off -line due to governor response problems, the Generation Entity shall immediately report the change in the status of the Resource to ERCOT and the QSE.

### 5.8.2	Primary Frequency Control Measurements

For the purposes of this section, the A Point is the last stable frequency value prior to a frequency disturbance.  For a decreasing frequency event with the last stable frequency value of 60.000 Hz or below, the actual frequency is used.  For a decreasing frequency event with the last stable frequency value between 60.000 and 60.036 Hz, 60.000 Hz will be used.  For a decreasing frequency event with the last stable frequency value above 60.036 Hz, actual frequency will be used.  For an increasing frequency event with the last stable frequency value of 60.000 or above, the actual frequency is used.  For an increasing frequency event with the last stable frequency between 59.964 and 60.000 Hz, 60.000 Hz will be used.  For an increasing frequency event with the last stable frequency value of 59.964 or below, the actual frequency is used.  ERCOT shall determine the A Point frequency for each event.

For the purposes of this section, the C Point is the lowest frequency value during thefirst few [do we need to use an actual number instead of “few”?] seconds of the event.

For the purposes of this section, the B Point is the “recovery” frequency value after the C Point.   The B Point should occur after full governor response of the turbines has occurred, usually between ten (10) and thirty (30) seconds after the A Point, but not greater than sixty (60) seconds after the A Point.  ERCOT shall determine the B Point for each event.

B Point Plus Thirty Seconds: At thirty seconds following the B Point, an analysis will be performed [by whom?] to determine if primary frequency control response is sustained.

For the purposes of this section, a “Measurable Event” is the sudden change in interconnection frequency that will be evaluated for performance compliance will have i) a frequency B Point between 59.700 Hz and 59.900 Hz or between 60.100 Hz and 60.300 Hz, and ii) a difference between the B Point and the A Point greater than or equal to +/- 0.100 Hz.

#### 5.8.2.1	ERCOT Required Primary Frequency Control Response

The combined response of all Generation Resources interconnected in ERCOT to a Measurable Event shall be at least 420 MW / 0.1 Hz. This value should be reviewed on an annual basis by ERCOT and the appropriate Market Participant group for system interconnect reliability needs.

This 420 MW / 0.1 Hz total primary frequency control response  will be proportionally assigned to all generation portfolios, by ratio share of each generation portfolio’s actual on line generation as compared to the sum of all actual on-linegeneration during the interval including the time of the A Point of the event.  Any Load that trips during an event that is included in a generation portfolio’s response will be subtracted from the generations portfolio’s total response.  This measurement applies to turbine response only.

ERCOT will evaluate, with the assistance of the appropriate Market Participant group,  generation portfolio participationduring sudden changes in Interconnection Frequency during Measurable Events.  The actual response of each generation portfolio will be compiled to determine if adequate primary frequency control participation was available.

ERCOT and the appropriate Market Participant group will review each Measurable Event, verifying the reasonableness of data, and tabulating generation portfolio participation.  Data that is in question may be requested from the QSE representing the generation portfolio for comparison and/or individual Resource data may be retrieved from ERCOT’s database.

A generation portfolio’s participation will be averaged using the most recent six (6) Measurable Events to determine their rolling average contribution.

#### 5.8.2.2

- .

### 5.8.3	ERCOT Data Collection

#### 5.8.3.1	Data Collection

ERCOT will collect all data necessary to analyze each Measurable Event.  This will include the following real-time  data:

- Interconnection Frequency;

- Regulation Service deployed;

- Responsive Reserve Service deployed;

- QSE available  Responsive Reserve Service;

- QSE total Generation;

- QSE SCE;

- QSE Bias;

- QSE LaaR MW;

- LaaR deployed;

- QSE Responsive Reserve Service; and,

- ERCOT Load and individual Resource(s) that contributed to the frequency deviation.