| PRR Number | 504PRR | PRR Title | Resource Derating Clarification |
| --- | --- | --- | --- |
| Date |  | 04/09/04 |  |
| Submitter’s Information |  |  |  |
| Name |  | Steve Myers |  |
| E-mail Address |  | smyers@ercot.com |  |
| Company |  | ERCOT |  |
| Company Address |  | TCC |  |
| Phone Number |  | 512.248.3077 |  |
| Fax Number |  |  |  |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

|  | Impact |  | Benefit |
| --- | --- | --- | --- |
|  | Business | Computer Systems |  |
| ERCOT | None | None | Improves relevancy of Resource data received by ERCOT. |
| MARKET SEGMENT | None | None | Not known |
| Consumer | None | None | Not known |
| LSE: General, Including NOIE | None | None | Not known |
| LSE: CR & REP | None | None | Not known |
| QSE | None | None | Same as Resource |
| Resource | None | None | Gives guidance on deration entry requirements |
| TDSP | None | None | Not known |

Comments

Deratings for fuel supply reasons, weather effects, and water supply issues that extend more than 48 hours (such as lake temperatures that represent high cooling water temperatures) are needed for Security Analysis studies for Transmission Outage Approval(s).

Deratings for fuel supply reasons (gas curtailments or shortages, need to burn standby fuel oil at a reduced capability, or wet weather causing lignite and coal handling problems), water issues (temperature, quality of water, or lack of water), and prolonged weather problems (such as needed deratings due to high ambient temperatures or severe weather conditions such as very cold conditions), can represent a significant amount of limitations to generation not otherwise shown as unavailable in the ERCOT system.  This significant amount would provide the wrong Security Assessment results in the Transmission Outage Approval Process, the support staff analyses, and, potentially, the real-time deployment algorithms used in ERCOT’s operating activities.

ERCOT suggests the following modifications to 504PRR:

Revised Proposed Protocol Language

### Deratings

The Resource Entity or its designee must enter material deratings that are expected to last more than forty-eight (48) hours in the ERCOT Outage Scheduler.  A derating is considered to be material when the Resource’s capability is reduced by 10 MW or more .  ERCOT will consider the Resource Entity’s capability as the lesser of the latest seasonal net capability test, or the asset registration submittal.