ercot impact analysis of the interval

data recorder requirements

January 4, 2004

Carl Raish

Lindsey Turns

Table of Contents

Introduction	3

Summary Conclusions and Recommendations	4

Methodology	6

Results	14

Benefits of Interval Data Recorders	43

APPENDIX A	52

APPENDIX B	57

APPENDIX D	65

APPENDIX E	68

# Introduction

Currently ERCOT Protocols, Section 18.6,”Mandatory Installation and Use of Interval Data Recorders”  specify the requirements for installing and using IDRs for settlement purposes.  In addition, the section requires ERCOT to perform an impact analysis of the IDR requirement; the implied purpose of the analysis is to evaluate modifications to the installation and use requirements as established at market open.  This report details the methods, results and conclusions of this analysis.

The analysis addressed three scenarios:

(1) The current requirement specifies that once an IDR is installed at a premise, it must remain there and be used for settlement purposes.  The first scenario consisted of analyzing the impact of establishing a demand threshold below which IDRs could voluntarily be removed.

(2) The current requirement specifies that an IDR shall be installed at a premise and used for settlement purposes when the premise peak demand is greater than 1000 kW (the second highest demand in a consecutive 12-month period is greater than 1000 kW).  The second scenario considered lowering the threshold for required installation.

(3)  The third scenario essentially combined the first two and considered lowering the required installation threshold and allowing voluntary removal of IDRs below that threshold.

The analytical process addressed the following criteria:

- Quantifying the impact to the market as a consequence of either increasing or decreasing profiling error by increasing or decreasing the number of premises and amount of load settled on profiles or with IDRs.

- Quantifying the premise level impacts associated with the changes to profiling error considering both the settlement impacts and TDSP charges specific to IDR metering.

- Quantifying the societal economic impact of the changes to profiling error by calculating the deadweight loss associated with alternative IDR thresholds (deadweight loss quantifies the cost to society of economic inefficiency associated with charging customers inaccurate prices).

- Assessing the system reliability benefits made available by providing more accurate price signals (resulting from the use of IDRs), reducing the requirement for generation capacity reserves and as a restraint on market power.

# Summary Conclusions and Recommendations

Conclusions

The primary conclusion of this analysis is that a significant amount of error in settlement cost could be eliminated by lowering the IDR installation threshold.  Lowering the installation threshold to 450 kW would cost approximately $575,000 on an annual basis and would eliminate an estimated $5.3 million dollars of Cross Customer Error per year.

Another important conclusion of the analysis is that allowing optional removal of IDRs for premises with peak demands below 1000 kW could introduce as much as $4.3 million of Cross Customer Error into settlement.  Since the removal would be optional, however, the likelihood of requests to remove all 3,752 IDRs is very remote.

A more likely result associated with allowing optional IDR removal would be for customers realizing TDSP tariff benefits to request removal.  With this consideration in mind, more realistic estimates would be to receive requests for 2,261 IDR removals, which would introduce $1.9 million of Cross Customer Error into settlement.

With respect to modifying the IDR threshold for installation or to allowing optional removal, the error costs as a percent of Total Settlement Cost would be quite small, less than 2%; thus the economic impact of any such changes would be small.

Several benefits, in addition to the settlement accuracy benefits discussed above, would be available to the market in association with retaining existing IDRs and lowering the installation threshold to add more.  These benefits, which are discussed but are not quantified, include UFE reduction, demand response benefits, improvement or maintenance of reliability, reduction in generation capacity reserves, and restraint on market power.

Recommendations

Based on the limitations of the supporting IDR data and to allow a gradual change in the market impact associated with installing IDRs and reading and processing the interval data, our recommendation is to initially set the IDR threshold at 700 kW.  At this level, about 964 IDRs would be need to be installed at a cost of $162,000 per year, and the Cross Customer Error reduction resulting from this would be about $2 million per year.

Optional removal of IDRs should be allowed at or below the 200 kW level.  Currently, 802 premises could be impacted by implementing this policy, but it is likely that no more than 364, who would see TDSP tariff charge reductions, would opt for removal.  TDSP tariff charges for these premises would be reduced by about $635 per premise, annual IDR costs of $168 per premise would be avoided and only $208 of Cross Customer Error per premise would be introduced into the settlement process.

Further analysis recommendations:

- Extend the mandatory installation analysis to a lower level (at least to 200 kW).

- Repeat the analysis taking into consideration the impact on UFE by modifying the IDR installation and removal thresholds, and incorporating the impact of UFE allocation on the calculation of settlement cost errors.

- Consider the impact of mandatory TOU metering and application of the profile chunking methodology as both an alternative and a supplement to IDR metering.  As part of this effort, incorporate the TOU Dead Weight Loss analysis to assess the societal benefit of IDR and TOU metering.  An example conclusion of this analysis might be to require TOU metering between 100 kW and 500 kW, and IDR metering above 500 kW.

- Repeat the analysis when ERCOT load research data is available to more accurately assess where the IDR threshold should be set.

# Methodology

The evaluation year for this analysis spanned May 1, 2002 through April 30, 2003 inclusive. Currently just fewer than 3,800 ESI IDs exist in ERCOT systems that had a peak demand of 1,000 kW or less during the analysis time frame.   ERCOT extracted IDR data for the analysis time frame for each ESI ID with an IDR and a peak demand not exceeding 1,000 kW during the same time frame.

Profiling Error and Impacts to Settlement Costs

The first analysis quantified the profiling error (kWh) that would be introduced into the settlement process as a result of settling an ESI ID on a profile instead of with actual interval data. For purposes of this analysis, the term “Profiling Error” refers to the energy differential that exists between the actual energy used and the energy allocated by the profile in any particular 15-minute interval. Several different measures were utilized to quantify the impact to the market of this profiling error, including Net Profiling Error Cost, Cross Customer Error, and Total Profiling Error Cost.

Once the interval data was compiled the first step in the analysis included calculating a load factor and assigning each ESI ID a profile type of BUSHILF (business high load factor), BUSMEDLF (business medium load factor), or BUSLOLF (business low load factor). The purpose for calculating the load factor was to determine which profile type would be used for settlement if the IDR meter were removed from the premise. The load factor calculation paralleled the Usage Month algorithm used to make assignments for Annual Validation.

The second step consisted of applying the ERCOT Data Aggregation process to simulated meter readings based on monthly aggregation of the interval data for each ESI ID and applying the usage to the appropriate profiles.  The energy was summed over the month for each ESI ID and a scaling factor was calculated by dividing the total monthly usage by the total monthly usage of the appropriate profile.  This scaling factor was then multiplied by every interval of the profile usage amount to scale the usage under the profile.

Settlement Costs

The third step consisted of computing Settlement Cost for each ESI ID based on its actual interval usage data and the corresponding market clearing price for energy; this cost was calculated as a basis for comparison of other calculated costs in the analysis.  This actual settlement cost for the premise as an IDR was found by:

SE=i=1Eiactual×MCPEi

where SE = Settlement Cost for an ESI ID ($),

Eiactual = Actual energy (kWh) for a 15-minute interval, and

MCPEi = Market Clearing Price of Energy for a 15-minute interval.

Fourthly, several measures of profiling error were determined.

Profiling Error

The Net Profiling Error was calculated by taking the difference of the actual interval energy and the profiled energy.  Thus the profiling error has a negative value where the profile overestimates the true usage and a positive value where the profile underestimates the true usage.  The Profiling Error for an ESI ID was found by:

PE=i=1Eiactual−Eiprofiled

where PE = Profiling Error (kWh) for an ESI ID,

Eiactual = Actual Energy (kWh) for a 15-minute interval, and

Eiprofiled = Profiled Energy (kWh) for a 15-minute interval.

Net Profiling Error Cost

The Profiling Error was used to calculate the Net Profiling Error Cost.  In this calculation the positive profiling errors and negative profiling errors from interval to interval cancel each other. Therefore this value, at the ESI ID level, indicates whether, at the end of the year, settling the premise with a profile would allocate higher or lower costs than would be allocated with IDR settlement.  The Net Profiling Error Cost for an ESI ID was calculated by:

NPEC=i=1PEi×MCPEi

where NPEC = Net Profiling Error Cost ($) for an ESI ID,

PEi = Profiling Error (kWh) for a particular 15-minute interval i, and

MCPEi = Market Clearing Price of Energy ($) for a particular 15-minute interval i.

The Net Error is the percentage of the Net Profiling Error Cost to the Settlement Cost and is found by:

NetError=NPECSE

where NPEC = the Net Profiling Error Cost ($), and

SE = the Settlement Cost ($).

Total Profiling Error

The Total Profiling Error for an ESI ID represents the total amount of Profiling Error due to misallocation of energy by the profiles. The absolute value of the Profiling Error for each interval was calculated and summed over the year for the ESI ID as shown below:

TPE=i=1Eiactual−Eiprofiled

where TPE = the Total Profiling Error (kWh),

Eiactual = Actual Energy (kWh) for an ESI ID for a 15-minute interval, and

Eiprofiled = Profiled Energy (kWh) for a 15-minute interval for an ESI ID.

The Total Profiling Error Cost for an ESI ID is:

TPEC=i=1TPEi×MCPEi

where TPEC = Total Profiling Error Cost ($),

TPEi = Total Profiling Error in a 15-minute interval, and

MCPEi = Market Clearing Price of Energy in a 15-minute interval.

Cross Customer Error

The next measure of error considered targets Profiling Error at the premise level. We have referred to this as Cross Customer Error (CCE); for an ESI ID, CCE was calculated by:

CCE=i=1PEi×MCPEi

where CCE = Cross Customer Error ($) for an ESI ID,

PEi = Profiling Error for a 15-minute interval, and

MCPEi = Market Clearing Price of Energy for a 15-minute interval.

At the ESI ID level, Cross Customer Error is the absolute value of the Net Profiling Error. Thus CCE accumulated over a group of ESI IDs, since it is always positive, is a measure of the total amount of settlement cost being incorrectly allocated to premises within the group.

The Cross Customer Error % is:

CCE%=CCESE

where CCE% is the Cross Customer Error Percent (%),

CCE = the Cross Customer Error ($), and

SE = Settlement Cost ($).

Table 1, shown below, illustrates the calculations discussed above for three sample ESI IDs.

Table 1. Example Profile Error Calculations

Dead Weight Loss

Dead Weight Loss (DWL) quantifies the societal cost of economic inefficiency associated with charging customers inaccurate prices as would tend to occur when premises are settled on profiles rather than with actual IDR data.  When the unit price faced by the customer is higher or lower than the true cost of providing electricity to the customer, the result is economic inefficiency.  The economic cost of price not being equal to the true cost of supply is known as “Deadweight Loss.”

There are two approaches with which to quantify incorrect price signals.  The first method considers that the average price per kWh over the year is off due to using load profiles rather than each customer’s interval data.  This effect is known as “flat pricing” DWL.  This theory assumes that the total annual consumption level customers choose is higher or lower than it would be if they were responsible for the true cost to supply them.  The second method considers the varying cost of energy due to time of day fluctuations.  This theory assumes that customers would consume differently during on- and off-peak times if they were faced with time-varying prices.  This effect is known as “TOU” DWL.

ERCOT performed the deadweight loss calculations based on flat pricing, using a modified formula for monthly energy weighted load profiled annual price. It should be noted that studies have shown the effect of TOU DWL is larger (by 5 to 20 times) than the effect of flat pricing DWL because the difference between on- and off-peak prices tends to be much greater than the difference in annual price based on a load profile versus individual load shape.   Appendix A provides more detail about computing DWL associated with flat pricing and on-/off-peak pricing.

First the load weighted average price of the profile was calculated using:

Upm=i=1MCPEi×kWhii=1kWhi

where Upm = load weighted average price for month m and profile p,

MCPEi = market clearing price of energy for interval i, and

kWhi = kWh in interval i.

Next the load profiled annual price for ESI ID j in profile p was calculated by:

Upj=i=112EjmUpmEj

where Upj = the load profiled annual price for ESI ID j,

Ejm = the energy (kWh) for ESI ID j in month m,

Upm = load weighted average price for month m, and

Ej = the total energy (kWh) for ESI ID j.

Deadweight loss is calculated using:

DWLflat=1/2eEjUpjUj−UpjUpj2

where e = elasticity of electricity demand with respect to the commodity price.

For purposes of this analysis, an elasticity of 0.122 was used.  See Appendix B for details on the assumptions and calculations associated with this value.

Estimates for Non-IDR Premises

The above statistics were computed directly for premises currently being settled with IDRs.  For premises with NIDR metering, estimates of each were needed to evaluate the impact of installing IDRs.  The ideal estimation method for these NIDR premises would be to pull data from concurrent representative load research samples and develop the corresponding statistics using domains analysis.  As a result of the lack of such data, we opted to use existing IDR data as a proxy sample; conclusions with respect to the NIDR population, thus should be taken as indicative and applied with caution.

For all ESI IDs in ERCOT systems with annual peak demand greater than

450 kW, monthly usage records were extracted covering the analysis period, May 1, 2002 through April 30, 2003.  For each ESI ID an ADUSE value was computed as outlined in the ERCOT Decision Tree for each day and summed to obtain an estimate of annual kWh.   The resulting annual kWh was categorized by profile type and demand level and summed accordingly.  Each of the statistics used to estimate the impact of IDR installation, Settlement Cost, Net Profiling Error, Dead Weight Loss, Cross Customer Error, and Total Profiling Error were then developed by applying the IDR ratios to annual kWh to the NIDR annual kWh.

Estimates for IDR Costs

For purposes of estimating the annualized incremental cost of IDR metering the following assumptions were made:

IDR Purchase/Installation		$1000

Annual Reading Cost		$72

Amortization Period			15 years

Interest Rate				5.0%

Annualized IDR Cost		$168

Current TDSP tariff charges for these vary considerably across jurisdictions; the costs being used in this analysis are based on current competitive industry quotes, and are believed to be more accurate reflections of true costs associated with IDR metering.

# Results

Impact of Establishing a Demand Threshold Below Which IDRs Could Voluntarily Be Removed

Tables 2  - 21 summarize the findings of analysis performed on all IDR data available for premises with a peak demand less than 1,000 kW during the analysis window. The first sets of tables quantify the impact of the various types of profiling error for all the premises.  Given that the option of removing IDRs would be voluntary, the errors reported represent a worst case scenario.  Later tables address the impact of selected subsets of IDRs being removed, so the intention with this analysis was to establish an upper bound which could be introduced for consideration.

Total Profiling Error

Table 2 shows the Total Profiling Error by demand level across all ESI IDs and Profile Types, and Table 3 shows the same results tabulated on a cumulative basis by demand level.  The results indicate that, for the 3,752 premises, approximately $50 million dollars of Total Profiling Error would be introduced into the settlement process.  This equates to approximately $13,000 of error per premise and about 22% of total settlement cost for this group.

The errors reported are large both in magnitude and percentage, but must be kept in perspective.  Clearly this error currently is zero since IDRs are in use for settlement purposes for all of these premises.  Since the Total Profiling Error is the sum of the absolute value of all the interval errors for all the premises, one must consider the impact of this error.  This impact at the system level is seen in tables 4 and 5, and at the premise level is seen in Tables 6 and 7.

Table 2.  Total Profiling Error Summary – All IDRs 0 kW to 1,000 kW

Table 3.  Cumulative Total Profiling Error Summary – All IDRs 0 kW to 1,000 kW

Net Profiling Error

Tables 4 and 5 below show the Net Profiling Error for these premises by demand level and cumulatively over demand level.  Since Net Profiling Error allows cancellation of profiling error to occur across customers, profile types and demand levels, the cumulative error at the system level can and does become very small, $13,000 total or $4 per premise.  A trend that becomes apparent, however, when looking at this level, is that low demand level premises tend to have their costs over-estimated while higher demand level premises tend to have their costs under-estimated.  While the net for the entire group ends up being only $4, within demand levels the net ranges from -$333 to $980 per premise.

Figure 1 illustrates the distribution of Net Profiling Error at the premise level which varies over a $21,000 range from -$13,540 to $7423.  In fact, just over 70% of the premises have Net Profiling Error Costs less than -$200 or greater than $200, the approximate annualized cost of IDR metering.  Figure 2 shows how the Net Profiling Error Cost in total is distributed across the range of error levels; in the case of this distribution, about 96% of the cost is distributed among premises having Net Profiling Error greater than $200.

Table 4.  Net Profiling Error Summary – All IDRs 0 kW to 1,000 kW

Table 5.  Cumulative Net Profiling Error Summary – All IDRs 0 kW to 1,000 kW

Figure 1.  Distribution of Net Profiling Error Summary – All IDRs 0 kW to 1,000 kW

Figure 2.  Distribution of Net Profiling Error Summary – All IDRs 0 kW to 1,000 kW

Cross Customer Error

Table 6 shows the Cross Customer Error for the same group of premises and Table 7 shows the results cumulatively.  Cross Customer Error is the net of profiling error within a premise over the analysis year, and thus allows over-estimation of load / cost in one interval to be off-set by under-estimation in another interval.  By allowing this within premise cancellation, it can be seen that about 90% of the Total Profiling Error is error within individual premises.  The Cross Customer Error, thus is a measure of the amount of settlement error that would be introduced by IDR removal and which is between premises.  As the Tables show, this error is still fairly substantial, about $4 million in aggregate, about 2% of total settlement cost and around $1100 per premise.

Table 6.  Cross Customer Error Summary – All IDRs 0 kW to 1,000 kW

Table 7.  Cumulative Cross Customer Error Summary – All IDRs 0 kW to 1,000 kW

Dead Weight Loss

Tables 8 and 9, shown below, summarize the Dead Weight Loss for these premises at the demand level and cumulatively over demand levels.  Since the elasticity assumed for these premises is quite low and since the premise level change in annual settlement cost between being profiled and settled with IDR data on a percentage basis is quite low, the resulting dead weight loss is quite low.  For this analysis the dead weight loss being computed is that attributed to annual consumption level and does not address TOU related dead weight loss.  Even given the likelihood that the TOU component could be significantly larger, it seems likely that there is a minimal societal economic benefit to retaining IDRs at these premises.  Stated another way, it is likely there would only be a minimal societal penalty associated with removing the IDRs.  Given the low annualized cost of IDR metering, however, a reasonable conclusion also would be that society should be ambivalent with respect both to installing and removing IDRs on these and similar premises.

Table 8.  Dead Weight Loss Summary – All IDRs 0 kW to 1,000 kW

Table 9.  Cumulative Dead Weight Loss Summary – All IDRs 0 kW to 1,000 kW

Retailer Impacts Associated with Voluntary IDR Removal

As stated, the previous results summarized analysis on all premises with peak demands less than 1000 kW to establish an upper limit on the impact.  Since the scenario being considered assumes optional IDR removal, the impacts ultimately will vary based on the specific premises that opt for removal.

As shown above, removing IDRs from some premises would result in a positive Net Profiling Error Cost (meaning the settlement costs are under-estimated) and for other premises the result would be a negative Net Profiling Error.  Consequently competitive retailers serving premises at which IDRs are removed would experience either lower or higher settlement costs depending on the characteristics of the premises they serve where IDRs are removed.

In the case of a CR deriving a settlement benefit because of IDR removal, however, it must be kept in mind, since the settlement in the ERCOT market is a zero-sum game, that those costs do not disappear, but are shifted to other CRs through UFE allocation.  Conversely, if a CR faces higher settlement costs as a result of IDR removal, that CR ends up subsidizing his competitors through the UFE allocation.

Table 10, shown below, summarizes the aggregate impact of IDR removal for premises that result in lower settlement costs (positive Net Profiling Error Cost) for the CR.  A total of 1,623 (43% of the total number) premises representing 48% of the total settlement cost fall in this category.  On a per premise basis the settlement cost reduction generally increases with demand level and ranges from $65 to $2500; the overall average per premise is $1300.  Net Profiling Error as a percent of total settlement cost is fairly uniform across demand levels and averages 2%. The sum of the Net Profiling error, that is the maximum total of subsidies to CRs serving these premises, would be $2.2 million.

Table 10.  Net Profiling Error Summary – All IDRs 0 kW to 1,000 kW with Lower Settlement Costs

Tables 11 – 13 break down the impact by profile type and show comparable per premise settlement reductions for BUSHILF and BUSMEDLF premises of about $1500; for BUSLOLF the settlement reduction is significantly lower at $624 per premise.  Net Profiling Error as a percent of total settlement cost does vary somewhat among the profile types, averaging 1.5% for BUSHILF, 2.4% for BUSMEDLF and 2.6% for BUSLOLF.

Table 11.  Net Profiling Error Summary – BUSHILF IDRs 0 kW to 1,000 kW with Lower Settlement Costs

Table 12.  Net Profiling Error Summary – BUSMEDLF IDRs 0 kW to 1,000 kW with Lower Settlement Costs

Table 13.  Net Profiling Error Summary – BUSLOLF IDRs 0 kW to 1,000 kW with Lower Settlement Costs

Table 14, shown below, summarizes the aggregate impact of IDR removal for premises that result in higher settlement costs (negative Net Profiling Error Cost) for the CR.  A total of 2,129 (57% of the total) number of premises representing 52% of the total settlement cost fall in this category.  On a per premise basis the settlement cost increase generally increases in absolute value terms (becomes more negative) with demand level and ranges from -$80 to -$2700; the overall average per premise is -$1007.  The percent of Net Profiling Error tends to decrease in absolute terms as demand level increases ranging from -3.2% to 1.4% and averages -1.8% across all premises. The sum of the Net Profiling error, that is the maximum total of the penalties to CRs serving these premises would $2.1 million.

Table 14.  Net Profiling Error Summary – All IDRs 0 kW to 1,000 kW with Higher Settlement Costs

Tables 15 – 17 break down the impact by profile type and show fairly comparable per premise settlement increases for all three profile types of about $1000. The percent of Net Profiling Error does vary somewhat among the profile types, averaging -1.1% for BUSHILF, -2.4% for BUSMEDLF and -3.7% for BUSLOLF.

Table 15.  Net Profiling Error Summary – BUSHILF IDRs 0 kW to 1,000 kW with Higher Settlement Costs

Table 16.  Net Profiling Error Summary – BUSMEDLF IDRs 0 kW to 1,000 kW with Higher Settlement Costs

Table 17.  Net Profiling Error Summary – BUSLOLF IDRs 0 kW to 1,000 kW with Higher Settlement Costs

Premise Impacts Associated with Voluntary IDR Removal

As shown above there is potential impact to the CR in terms of settlement cost associated with IDR removal; consequently, CRs could realize some benefit in terms of lower settlement costs by carefully targeting premises for removal.  To the extent competitive forces are effective in the market, such cost reductions would tend to be both sought by and passed down to the customer level.

In addition, customers currently are likely to be exposed and tend to react to TDSP related charges associated with IDR metering.  In fact, these TDSP charges are likely to be more visible to the customer and thus carry a higher weight in terms of deciding whether to retain or request removal of an IDR.  For purposes of this analysis TDSP tariff metering service charges and transmission service charges were computed for each current IDR premise with a peak demand less than 1000 kW based on the TDSP providing the service.  Tariff charges were computed based on the premise having both IDR and NIDR metering, and the differences in charges were compared.  Premises were grouped into two categories: (1) those that would experience increased monthly charges (over the course of a year) by removing the IDR meter and (2) premises that would experience decreased charges (over the course of a year) by removing their IDR meter.

The results of this comparison are shown in Tables 18 and 19 below.  A total of 2,261 (61% of the total) premises would incur lower TDSP tariff charges by removing their IDR meters.  The average annual reductions across demand levels would range from $580 to $2500 and would average $1600 across all these benefiting premises.  If all of these premises were to have their IDRs removed, the total reduction in TDSP tariff charges would be $3.6 million.

A total of 1,464 (39% of the total) premises would incur higher TDSP tariff charges by removing their IDR meters.  The average annual increases across demand levels would range from $110 to $3500 and would average $1373 across all such premises.

Table 18.  IDR versus Non-IDR Meter Charges for Premises where Monthly Tariff Charges Would Decrease by Removing IDR Meter

Table 19.  IDR versus Non-IDR Meter Charges for Premises where Monthly Tariff Charges Would Increase by Removing IDR Meter

Tables 20a and 20b focus on premises which would incur lower tariff charges; Table 20a summarizes the impact associated with IDR removal for premises that would end up with lower settlement costs and Table 20b summarizes the results for those with higher settlement costs.  Premises are split virtually the same in terms of numbers between those with lower and higher settlement costs.  If all premises with lower settlement costs were to have their IDR metering removed, the total Net Profiling Error cost would be $1.2 million, or about $1000 per premise.  If all premises with higher settlement costs were to have their IDR metering removed, the total Net Profiling Error cost would be -$0.7 million, or about -$650 per premise.

Taking both groups together, a total of about $1.9 million dollars would be moved back and forth among CRs in the form of subsidies and penalties.  Table 21 combines the Cross Customer Error for the two different groups.

Table 20a. Profiling Error Summary – IDRs with Lower Tariff Charges and Lower Settlement Costs

Table 20b.  Profiling Error Summary – IDRs with Lower Tariff Charges and Higher Settlement Costs.

Table 21. Cumulative Cross Customer Error Summary – IDRs with lower Tariff Charges

Complete tables for the Impact of Establishing a Demand Threshold Below Which IDRs Could Voluntarily Be Removed analysis can be found in Appendix C.

Mandatory IDR Installation Threshold

The previous section reviewed the impact of removing IDRs from premises where they are currently installed.  This section shifts to a review of the impact of installing IDRs at premises currently settled on NIDR meters.  The estimation process for the comparative statistics is described in the Methodology section.  The results shown below should be taken as useful indications of the impact of lowering the IDR installation threshold and not as conclusive results.

The tables shown below summarize the estimates developed across all ESI IDs with NIDR metering and with annual peak demands between 450 – 1000 kW; the results are also shown cumulatively over demand levels in descending order to facilitate analyzing the impact for various installation thresholds.

Total Profiling Error

Table 22 shows the Total Profiling Error by demand level for the selected ESI IDs with NIDR metering; Table 23 shows the results for Total Profiling Error cumulatively.  As is shown, 3,419 premises were identified, which account for $271 million of Total Settlement Cost.  The estimated Total Profiling Error for these premises is about $64 million; this equates to approximately $18,700 of error per premise and about 24% of Total Settlement Cost for this group.

As with the IDR removal analysis, these errors are large both in magnitude and percentage, but must also be kept in perspective.  Clearly this error would go to zero if IDRs were installed at all the premises and used for settlement purposes. Since the Total Profiling Error is the sum of the absolute value of all the interval errors for all the premises, one must consider the impact of this error.  This impact at the premise level is seen in Tables 24 and 25 and at the system level in Tables 28 and 29.

Table 22.  Total Profiling Error Summary - All NIDRs 450 kW to 1,000 kW

Table 23.  Cumulative Total Profiling Error Summary - All NIDRs 450 kW to

1,000 kW

Cross Customer Error

Table 24 shows the Cross Customer Error for the same group of premises and Table 25 shows the results cumulatively over demand levels.  Cross Customer Error is the net of profiling error within a premise over the analysis year, and thus allows over-estimation of load / cost in one interval to be off-set by under-estimation in another interval.  By allowing this within premise cancellation, it can be seen that about 90% of the Total Profiling Error is error within individual premises.  Cross Customer Error, thus, is a measure of the amount of settlement error that would be eliminated by IDR installation on these premises which is between premises.  As the Tables show, this error is still fairly substantial, about $5.3 million in aggregate, about 2% of total settlement cost and around $1500 per premise.  The Cross Customer Error is closely correlated with demand level and ranges from the high $2000 per premise at the upper demand levels and drops off to about $1000 at the 450 – 500 kW level.

On a cumulative basis, the Cross Customer Error is consistently and significantly higher than the annualized cost of IDR metering, even down to the 450 kW level.

Table 24.  Total Cross Customer Error Summary - All NIDRs 450 kW to 1,000 kW

Table 25.  Cumulative Total Cross Customer Error Summary - All NIDRs 450 kW to 1,000 kW

Dead Weight Loss

Tables 26 and 27, shown below, summarize the Dead Weight Loss for these premises at the demand level and cumulatively over demand levels.  As with the IDR removal analysis, since the elasticity assumed for these premises is quite low and since the premise level change in annual settlement cost between being profiled and settled with IDR data on a percentage basis is quite low, the resulting dead weight loss is quite low.  For this analysis the dead weight loss being computed is that attributed to annual consumption level and does not address TOU related dead weight loss.  Even given the likelihood that the TOU component could be significantly larger, it seems likely that there is a minimal societal economic benefit to installing IDRs at these premises.  Given the low annualized cost of IDR metering, however, a reasonable conclusion also would be that society should be ambivalent with respect both to installing or not installing IDRs on these premises.

Table 26.  Total Dead Weight Loss Summary - All NIDRs 450 kW to 1,000 kW

Table 27.  Cumulative Total Dead Weight Loss Summary - All NIDRs 450 kW to 1,000 kW

Net Profiling Error

Tables 28 and 29 below show the Net Profiling Error for these premises by demand level and cumulatively over demand level.  Since Net Profiling Error allows cancellation of profiling error to occur across customers, profile types and demand levels, the cumulative error at the system level can and does become quite small, $434,000 total or $127 per premise and much less than 1% of Settlement cost. A trend that becomes somewhat apparent, however, when looking at this level, is that the Net Profiling Error Cost is generally positive indicating that these premises tend to have their costs under-estimated.  While the net for the entire group ends up being only $127, within demand levels the net ranges from -$123 to $940 per premise.

Table 28.  Total Net Profiling Error Summary - All NIDRs 450 kW to 1,000 kW

Table 29.  Cumulative Total Net Profiling Error Summary - All NIDRs 450 kW to 1,000 kW

Complete tables for the Mandatory IDR Installation Threshold analysis can be found in Appendix D.

Combination Mandatory Installation and Optional Removal

This section presents the results of the two previous sections combined to reflect the impact of establishing a threshold above which IDR installation would be mandatory and below which removal would be available on a voluntary basis.  To quantify the combined impact, errors introduced from IDR removal are added to the errors that would be eliminated by IDR installation at the profile type and demand level.  The estimation process for the comparative statistics is described in the Methodology section.  Keep in mind that the two previous caveats still apply; (1) the option of removing IDRs would be voluntary and therefore the errors reported represent a worst case scenario, and (2) the results shown below should be regarded as indications of the impact of lowering the IDR installation threshold and not as conclusive results.

The tables shown below summarize the estimates developed by demand level for the combination of all ESI IDs with IDRs with annual peak demands under 1000 kW and ESI IDs with NIDR metering and with annual peak demands between 450 – 1000 kW (essentially all ESI IDs between 450 kW and 1000 kW); the results are also shown cumulatively over demand levels in descending order to facilitate analyzing the impact for various installation thresholds.

Total Profiling Error

Table 30 shows the Total Profiling Error by demand level.  Table 31 shows the results for Total Profiling Error cumulatively.  As is shown, 5,249 premises were identified, which account for $442 million of Total Settlement Cost.  The estimated Total Profiling Error for these premises is about $100 million; this equates to approximately $19,200 of error per premise and about 23% of Total Settlement Cost for this group.

As with the IDR removal analysis, these errors are large both in magnitude and percentage, but must also be kept in perspective.  Clearly this error would go to zero if IDRs were installed at all the premises and used for settlement purposes. Since the Total Profiling Error is the sum of the absolute value of all the interval errors for all the premises, one must consider the impact of this error.  This impact at the premise level is seen in Tables 32 and 33 and at the system level in Tables 36 and 37.

Table 30.  Total Profiling Error Summary - All IDRs 0 kW to 1000 kW Plus NIDRs 450 kW to 1000 kW

Table 31.  Cumulative Total Profiling Error Summary - All IDRs 0 kW to 1000 kW Plus NIDRs 450 kW to 1000 kW

Cross Customer Error

Table 32 shows the Cross Customer Error for the same group of premises and Table 33 shows the results cumulatively.  Cross Customer Error is the net of profiling error within a premise over the analysis year, and thus allows over-estimation of load / cost in one interval to be off-set by under-estimation in another interval.  By allowing this within premise cancellation, it can be seen that about 90% of the Total Profiling Error is error within individual premises.  The Cross Customer Error, thus is a measure of the amount of settlement error that would be eliminated by IDR installation on these premises which is between premises on an annual basis.  As the Tables show, this error is still fairly substantial, about $8.4 million in aggregate, about 2% of total settlement cost and around $1600 per premise.  The Cross Customer Error is closely correlated with demand level and ranges from the high $2600 per premise at the upper demand levels and drops off to about $1100 at the 450 – 500 kW level.

On a cumulative basis, the Cross Customer Error is consistently and significantly higher than the annualized cost of IDR metering, even down to the 450 kW level.

Table 32.  Cross Customer Error Summary – All IDRs 0 kW to 1000 kW Plus NIDRs 450 kW to 1000 kW

Table 33.  Cumulative Cross Customer Error Summary – All IDRs 0 kW to 1000 kW Plus NIDRs 450 kW to 1000 kW

Dead Weight Loss

Tables 34 and 35 shown below summarize the Dead Weight Loss for these premises at the demand level and cumulatively over demand levels.  As with the previous two analyses, since the elasticity assumed for these premises is quite low and since the premise level change in annual settlement cost between being profiled and settled with IDR data on a percentage basis is quite low, the resulting dead weight loss is quite low.  For this analysis the dead weight loss being computed is that attributed to annual consumption level and does not address TOU related dead weight loss.  Even given the likelihood that the TOU component could be significantly larger, it seems likely that there is a minimal societal economic benefit to installing IDRs at these premises.  Given the low annualized cost of IDR metering, however, a reasonable conclusion also would be that society should be ambivalent with respect both to installing or not installing IDRs on these premises.

Table 34.  Total Dead Weight Loss Summary - All IDRs 0 kW to 1000 kW Plus NIDRs 450 kW to 1000 kW

Table 35.  Cumulative Total Dead Weight Loss Summary - All IDRs 0 kW to 1000 kW Plus NIDRs 450 kW to 1000 kW

Net Profiling Error

Tables 36 and 37 below show the Net Profiling Error for these premises by demand level and cumulatively over demand level.  Since Net Profiling Error allows cancellation of profiling error to occur across customers, profile types and demand levels, the cumulative error at the system level can and does become quite small, $743,000 total or $142 per premise and much less than 1% of Settlement cost. A trend that becomes somewhat apparent, however, when looking at this level, is that the Net Profiling Error Cost is generally positive indicating that these premises tend to have their costs under-estimated.  While the net for the entire group ends up being only $142, within demand levels the net ranges from -$158 to $958 per premise.

Table 36.  Net Profiling Error Summary - All IDRs 0 kW to 1000 kW Plus NIDRs

450 kW to 1000 kW

Table 37.  Cumulative Net Profiling Error Summary - All IDRs Plus NIDRs 450 kW to 1000 kW

Complete tables for the Combination Mandatory Installation and Optional Removal analysis can be found in Appendix E.

# Benefits of Interval Data Recorders

This section provides an overview of potential benefits of interval data recorders (IDRs).  The discussion is not intended to be definitive, nor to provide quantitative estimates of the value of increasing the number of ESIIDs with IDRs.  Rather, the intent is to identify the issues that can be considered, from the perspectives of end-use customers, TDSPs, CRs, ERCOT itself, and society as a whole.

Most of the available literature identifies benefits to customers, utilities, and society.  In the ERCOT market, the “utility” role is split between TDSPs and CRs.  ERCOT itself also plays some of this role.

Many of the benefits of IDRs depend on customers’ paying a price for electricity that varies by time interval (e.g., by hour or quarter-hour).  These benefits do not derive simply from the fact that the cost of electricity varies by time interval, but are contingent on customers paying a price for electricity that varies by time interval.  Furthermore, some of the benefits of IDRs depend on customers changing the quantity of electricity they demand in response to the price signals they receive.  Specifically, customers respond to an increase in price by decreasing the quantity of electricity they demand.

The following table summarizes various benefits of interval data recorders.  Where estimates of the magnitude of the benefit are available from the literature, these are also indicated.  However, further work would be needed to translate these indicative values into specific estimates of the value to the ERCOT market.  Each of these benefits is described in brief below.

Summary of IDR Benefits

| Benefit Category | Benefit | To Whom Benefits Accrue | Estimated Value |
| --- | --- | --- | --- |
| Reduce cost of economic inefficiency (deadweight loss) | Increased economic efficiency (Avoided deadweight loss) | Society | Case-specific |
| Reduce unaccounted-for-energy (UFE) | Avoided UFE costs | Society | 1.5 cents/kWh (Absolute UFE costs) (unpublished analysis by ERCOT LPWG) |
| Improve/maintain reliability | Value to the customer of maintaining load | Customer | $2,600 - $22,000 per MWh (2002 US $) [Cooke (2003)] |
|  | Avoided electricity rationing costs | ISO/TDSP/REP/ Customer | No generic cost estimates available in literature |
|  | Avoided costs of restoring power | ISO/TDSP/ Customer | $20 million annually in crew dispatch costs for medium-sized utility dealing with Sustained Outages. [Bishop, McCarthy & Rose (1998)] |
|  | Avoided damage to utility and/or ISO reputation as reliable service provider | ### TDSP/REP/ISO | No generic cost estimates available in literature. |
|  | Avoided payments resulting from reliability-related lawsuits | TDSP/ISO/REP/ Other potentially liable parties | No generic cost estimates available in literature. However, Ohio utility FirstEnergy’s stock value dropped 2% the day following the release of report on August 2003 power outage that implicated the utility. |
|  | Avoided/reduced Performance-Based Ratemaking (PBR) reliability penalties | TDSP | Potential financial penalties of $2 - $36 million per year per utility (for those utilities with financial penalties for PBR violations) [KEMA-XENERGY (2001)] |
| Reduce cost of maintaining reliability | Replacement of generation capacity reserves with less expensive demand-side resources | Retail Electricity Providers/ Customer | No generic cost estimates available in literature. |
| Restrain market power | Reduced market power by facilitating customer response to price | Society | No generic cost estimates available in literature. |

Reduced Societal Cost of Economic Inefficiency (Deadweight Loss)

If a customer pays a price for electricity that varies by time period and has an IDR, then the customer has the necessary price signals to determine the quantity of electricity they will demand.  This is the benefit captured by the deadweight loss analysis.

Reduced UFE

Another benefit of IDRs is a more accurate accounting of load by time period.  This will reduce the contribution of inaccuracies in settled load to unaccounted-for-energy (UFE) each time period.  UFE is system load minus settled load and allocated losses by time period.

Demand Response Benefits

Other benefits of IDRs depend on customers responding to an increase in price by decreasing the quantity of electricity they demand.  Three benefits that fall into this category are:

improvement or maintenance of reliability,

reduction in required generation capacity reserves, and

restraint of market power.

Each of these benefits is discussed briefly in turn.

Improvement or maintenance of reliability

If the quantity of electricity demanded is lower than it would otherwise be, reliability is improved or maintained by reducing the likelihood of a power outage.  The value of improved or maintained reliability, then, is the value of reducing the number of power outages.

The costs of a power outage include:

- the cost to customers,

- the cost of allocating the scarce supply of electricity when a power outage occurs,

- the cost of restoring power,

- the damage to the utility’s and independent system operator’s reputations as reliable service providers,

- payments resulting from lawsuits related to the power outage, and

- performance-based ratemaking (PBR) reliability penalties.

## Cost to customers

The cost to customers of a power outage has been estimated to be between $2,600 and $22,000 per MWh (Cooke 2003).  Allan and Srbac (2001) provide a list of costs that may be included in such an estimate:

- Direct economic costs

  - lost production

  - idle resources

  - restart costs

  - spoilage

  - equipment damage

  - health & safety costs

  - utility interruption costs

- Direct social costs

  - loss of transport

  - loss of leisure

  - lack of heating/cooling

  - personal injury

- Indirect losses

  - civil disobedience

  - evacuation for safety

- Short term/ long term

  - future mitigation decision

  - extra protection/ standby

  - relocation costs

Customer outage costs may be offset by payments from conventional insurance policies, special outage insurance offered by some utilities, and rewards from successful lawsuits.  Backup generators and other power quality measures can also mitigate customer outage costs.

Primen (2002) found the cost of a power outage is strongly correlated to the size of the business establishment.  The average cost of a one-hour outage increases steadily as a function of the establishment's annual kWh consumption.  The study also found the outages costs for a one-hour outage are about four times that for a three minute outage.

The costs identified by Allan and Srbac (2001) are the actual costs of a power outage to customers.  In addition, EIA (1995) points out another cost to customers of a power outage is the “lost surplus” cost. This hypothetical cost represents the excess above the price of electricity that consumers were willing to pay for the electricity not supplied during an outage.  For example, if a consumer was willing to pay 10 cents/kWh for electricity that was not supplied, but the price of electricity not supplied was only 6 cents/kWh, then the lost surplus cost is 4 cents/kWh.  Lost surplus costs are difficult to estimate because they cannot be measured directly and, therefore, are seldom included in the calculation of customer power outage costs.

The cost to customers of a power outage is often given as a range because it depends on many factors including:

- the activities/mix customers affected by the curtailment, which depends on what day and what time of the outage occurs;

- whether or not there was advanced warning;

- weather conditions;

- time of year; and

- duration of the outage.

Common methods for estimating the cost to customers of a power outage include:

- indirect analytical methods using associated indices or variables (e.g., dividing gross domestic product by total energy consumed);

- customer surveys including those using contingency valuation methods; and

- detailed studies of costs incurred by customers during power outages.

Customer surveys often produce contradictory results.  For example, residential customers give much lower values when asked how much they are willing to pay for more reliability than when asked how much they are willing to accept to be compensated for less reliability. Also, a survey of commercial/industrial customers in England found very high estimates of the value of avoiding a power outage even though very few of the respondents had purchased backup generators.

Cost of rationing

We did not find in the literature any estimates of the cost of allocating the scarce supply of electricity when a power outage occurs.  This cost is borne by the ISO/TDSPs/REPs/investors and/or end-use customers depending on the extent to which it is recoverable in rates at different levels.

Cost of restoring power

The annual cost of restoring power has been estimated to be in the neighborhood of  $20 million (Bishop, McCarthy, and Rose 1998).  This estimate is based on:

- 10,000 sustained outages per year,

- each sustained outage requires 4 hours of crew time, and

- the cost for a crew and repair truck is $500/hr.

The cost of restoring power is generally recoverable through rates unless the utility is found to be grossly negligent.  Therefore, this cost is typically borne by customers.

Damage to the ISO/utility’s reputation as a reliable service provider

The cost of the damage to the ISO or utility’s reputation as a reliable service provider is difficult to quantify.  This cost may include elements such as:

- cost of increased regulatory scrutiny,

- reduced investment appeal (measured by the reduction in utility stock value and bond ratings),

- value of customers lost to competitive suppliers, and

- additional utility public relations and marketing expenditures designed to restore regulator, investor, and customer confidence.

For example, the value of FirstEnergy’s stock dropped 2.1 percent the day after the U.S./Canada Power System Outage Task Force issued its initial report on the August 2003 power outage, which assigned significant culpability to the utility.  (This is the only estimate of the cost of the damage to the utility’s reputation as a reliable service provider we found in the literature.)

Payments resulting from lawsuits related to power outages

Reductions in both a utility's stock value and bond rating may reflect investor assessment of utility's potential liability.  The cost of payments resulting from lawsuits related to power outages is unlikely to be recoverable in utility rates and, therefore, is likely to be borne by the utility/investors.  It is unclear how any costs of lawsuits against ERCOT would ultimately be borne.

PBR reliability penalties

Some utilities with PBR mechanisms must pay a predefined monetary penalty when the frequency or duration of outages exceed certain predetermined threshold levels (PBR reliability penalty).  A 2001 KEMA-XENERGY study of utilities with PBR mechanisms found the maximum potential annual penalty for reliability violations ranged from $2 million (Narragansett Electric) to as much as $36 million (Southern California Edison).  Although these figures are only potential penalties, utilities have been required to pay PBR reliability penalties.  For example, in September 2003, Massachusetts Electric was assessed a $5.9 million PBR reliability penalty.  Even if TDSPs do not currently have PBR structures, this could become an issue in the future.

Reduction in required generation capacity reserves

IDRs facilitate participation in demand-response programs.  With greater participation in demand-response programs, more demand-side resources are available to replace potentially more expensive generation capacity reserves.

Restraint on market power

The ability of suppliers to set price above marginal cost is referred to as market power and results in the wrong quantity of electricity supplied/consumed.  Market power may be restrained if customers, facilitated by IDRs, respond to an increase in price by decreasing the quantity of electricity they demand.  If the quantity of electricity that suppliers sell is affected by the price they charge, they may choose to charge a lower price.

Reference List

Besser, Janet Gail.  2000.  “The Value of Load Response in Competitive Markets: The Importance of Efficient Electricity Price Signals.”  Hartford, Connecticut (October).

Billington, Roy.  2002.  “Economic Cost of Non-Supply.”  Power System Research Group, University of Saskatchewan, Canada.

Bishop, Martin T.; Christopher A. McCarthy; and Virgil G. Rose.  1998.  “Distribution Reliability Improvement Cost Justification.”  Cooper Power Systems, Systems Engineering Reference Bulletin SE 9801 (November).

Brennan, Timothy.  2002.  “Market Failures in Real-Time Metering: A Theoretical Look.”  Resources for the Future, Discussion Paper 02-53 (October).

Cooke, J. Alexander.  2003.  “The resource adequacy requirement in FERC's standard market design: Help for competition or a return to command and control?”  Yale Journal on Regulation (Summer).

Cramton, Peter; and Jeffrey Lien.  2000.  “Value of Lost Load.”  University of Maryland (February).

Cummings, Fran.  2000.  Memorandum to John Chamberlin, Henry Yoshimura, and Christopher Dyson of XENERGY Inc.  Summary of Price Responsive Load in the Northeast: 16 October 2000 ISO Meeting at Hartford, Connecticut (November).

de Noojj, Michiel; Carlijn Bijvoet; and Carl Koopmans.  “The Demand for Supply Security.”  SEO, Amsterdam Economics, University of Amsterdam.

Energy Information Administration.  1995.  “Performance Issues for a Changing Electric Power Industry” in Appendix B, The Economics of Electric Power Reliability (January).

Energy Research Institute, Chulalongkorn University.  2001.  “The Future Value of Lost Load and its Applications” in Electricity Outage Cost Study.  http://www.eppo.go.th/power/ERI-study-E/ERI-ExeSummary-E.html.

Felder, Frank.  2001.  “An Island of Technicality in a Sea of Discretion: A Critique of Existing Electric Power Systems Reliability Analysis and Policy.”  Electricity Journal (10 January).

Goldman, Charles A.; Michael Kintner-Meyer; and Grayson Heffner.  2002.  “Do ‘Enabling Technologies’ Affect Customer Performance in Price-Responsive Load Programs?”  Ernest Orlando Lawrence Berkeley National Laboratory: Berkeley, California (August).

Hirst, Eric.  2003.  “Long-Term Resource Adequacy: The Role Of Demand Resources.”  (January).

Lee, Russell.  2002.  “Ideas on a Framework and Methods for Estimating the Benefits of Government-Sponsored Energy R&D.”  Oak Ridge National Laboratory: Oak Ridge, Tennessee (27 February).

Moeltner, Klaus; and David F. Layton.  2002.  “A Censored Random Coefficients Model for Pooled Survey Data With Application to the Estimation of Power Outage Costs” in Review of Economics & Statistics (August): 552-561.

Moran, Alan.  “Application for Authorization: Value of Lost Load.”  Institute of Public Affairs’s submission to the ACCC Review of the Electricity Price Cap.  [New Zealand?].

National Electricity Code Administrator Limited.  2002.  “Reliability Panel: Review of the value of lost load.” Consultation paper (December).

National Electricity Code Administrator Limited.  2003.  “Reliability Panel: Review of the value of lost load” (June).

Pacificorp and ABB Consulting.  2003.  “Engineering Tools Move into Cyberspace.”  http://tdworld.com/ar/power_engineering_tools_move/index.htm.  (1 March).

Primen.  2002.  “Power Quality Problems and Renewable Energy Solutions” submitted to Massachusetts Renewable Energy Trust (September).

Sedano, Richard P.  2001.  “Dimensions of Reliability: A Paper on Electric System Reliability For Elected Officials.”  National Council on Competition and the Electric Industry, The Electric Industry Restructuring Series (October).

Stephenson, W.M.; and D.J. Barney.  1988.  “Economics of energy reliability.”  Pacific Gas & Electric Company.  Potentials (San Francisco, California) 7 (May): 26-27.

Strbac, Goran; and Ron Allan.  2001?.  “Customer Worth of Supply and Application to Future Regulation of Distribution Systems.”  Manchester Centre for Electrical Energy, UMIST.

Sullivan, Michael; and Michael Sheehan.  2000.  “Observed Changes in Residential and Commercial Customer Interruption Costs in the Pacific Northwest Between 1989 and 1999.”  IEEE.

XENERGY, Inc.  2001.  Performance-Based Ratemaking: Companion Study.  XENERGY, Inc.: Burlington, Massachusetts (January).

Appendices

# APPENDIX A

Calculating the Cost of Economic Inefficiency Due to

Lack of Interval Meters

Overview

When the unit price faced by the customer is higher or lower than the true cost of providing electricity to the customer, the result is economic inefficiency.  In this situation, it is theoretically possible to make everyone better off.  The economic cost of price not being equal to the true cost of supply is known as the “Deadweight Loss.”  This is a cost borne by society as a whole, which benefits no one.  In principle, if prices were all moved to the true costs of supply, the negative effects of the price shifts for certain parties (customers previously underpaying or suppliers previously receiving overpayments) could be compensated by those who benefit from this change, and the elimination of deadweight loss would result in additional resources that could be employed to everyone’s benefit.

We consider two components of price signal errors, and associated societal cost of inefficiency.

- The annual average unit cost of energy based on the load profile is different from each ESIID’s true annual average cost per unit consumed.  This price signal error results in over-or under-consumption over the course of the year.

- Customers without interval metering face prices that are not differentiated by time of day, whereas supply costs do vary by time.  This price signal error results in over-consumption during periods of high market prices, and under-consumption during periods of low market prices, even for a fixed total consumption level.

(Some customers do have time-of-use (TOU) metering, though they do not have interval demand recorders (IDR).  In principle, even these customers could have more finely differentiated prices.  The economic inefficiency due to lack of more time-specific pricing for TOU ESIIDs is less than that for nonTOU ESIIDS, but still exists.)

## Cost to the Economy of Wrong Price Signals on Average for the Year

For any commodity, the deadweight loss due to assigning each customer the load-profiled annual price ULPj instead of assigning each customer its own true cost of supply Uj depends on the differences between the load profiled prices and the customers’ true cost of supply, as well as on the customers’ consumption and the elasticity of demand with respect to price.  This deadweight loss can be calculated separately for each load profile p and demand level k.  (Equation A).

(A)	DWLFLATkp = ½ eAkpEpkjkp Ej Upj ((Uj – Upj)/Upj)2 /Epk

where

eAkp = elasticity of annual consumption with respect to price, for ESIIDs in demand level k, profile p

Ej = annual energy consumption for ESIID j

Epk = total annual energy consumption of ESIIDs j in demand level k, profile p

Uj = load weighted annual price using true interval data for ESIID j

Upj = load weighted annual price for ESIID j using load profile p

DWLFLATkp = Deadweight loss ($/year) due to load profiling error in the annual unit price of energy, for ESIIDs in demand level k, load profile p.

The deadweight loss can also be expressed in terms of cost per unit of energy consumption (Equation B).  This formulation provides a useful basis for comparison with other costs.

(B)	DWLUFLATkp =  ½ ekpjkp Ej Upj ((Uj – Upj)/Upj)2 /Epk

where

DWLUFLATkp = Unit deadweight loss ($/MWh) due to load profiling error in the annual price cost of energy, for ESIIDs in demand level k, load profile p.

The unit deadweight loss given by Equation B is the societal cost of the economic efficiency due to inappropriate price signals on average over the year.  The price response in this calculation is assumed to affect the total amount of electricity consumed, but not the pattern of that consumption over the year.

## Modified Formula Using Monthly Adjusted Load Weighted Prices

If we use the monthly energy weighted load profiled annual price, this price varies across ESIIDs j within the same load profile p, according to the distribution of monthly energy Ejm over the year.  That is, the load profiled annual price for ESIID j in profile p is given by

(C)	Upj = m=112 Ejm Upm/Ej

where

Upm is the profile load-weighted price for month m.

In this case, the DWL formula becomes

(D)	DWLFLATkp = ½ ekpjkp Ej Upj ((Uj – Upj)/Upj)2

= ½ ekpEpkjkp Ej Upj ((Uj – Up)/Up)2 /Epk

or on a per-energy-unit basis

(E)	DWLUFLATkp =  ½ ekpjkp Ej Upj ((Uj – Up)/Up)2 /Epk

## Cost to the Economy of Lack of Time-Differentiated Priced Signals

An additional source of economic inefficiency and deadweight loss results from not offering customers time-dependent price signals.  Even if the flat unit price charged is correct on average over the year, there are times when this flat price is higher than the true cost of supply and times when it is lower.  If consumers saw this price difference, rather than always facing the same flat price, they would tend to shift some load from higher to lower cost periods.  That is, they would cross-substitute consumption during low cost periods for consumption during high cost periods.

Benefits of time-dependent pricing include load shifting and associated effects on capacity requirements, network congestion, transmission and distribution investments, reserve margins, and load factors.  If markets are functioning well, so that market prices are a meaningful reflection of all the components of supply costs, the load shifting benefits for generation capacity, congestion, transmission and distribution sizing, reserves, and load factors should in principle be reflected in the hourly market prices of the commodity.  This view is somewhat of a simplification, inasmuch as some of these benefits will be seen in the markets for ancillary services, not simply in the wholesale energy market.  However, wholesale energy prices do substantially reflect these other costs as well.

Thus, the cost of economic inefficiency due to lack of time-dependent pricing can be quantified in terms of a similar deadweight loss analysis.  In this case, the deadweight loss depends on the difference between the wholesale cost of energy in each interval and the flat annual average cost.  In principle, deadweight loss could be calculated for each quarter-hour interval in terms of the difference between the true interval price and the assigned flat price.  Such an analysis would need to consider the interval elasticities of the demand response, as well as the potential for load shifting between intervals rather than simple increases and decreases in overall consumption level.  Apart from the complexity of the analysis, it would be essentially impossible to obtain meaning cross-period elasticities on a quarter-hourly interval basis.

Instead, we consider the primary benefit of time-dependent pricing, namely differentiating on- and off-peak consumption.  The deadweight loss related to giving customers flat prices instead of separate on- and off-peak prices captures the economic value of load shifting.  If the interval market prices appropriately incorporate transmission, capacity, and congestion costs, the corresponding deadweight loss calculation appropriately captures the economic benefit related to these factors.

To first order, the deadweight loss due to lack of TOU pricing can be calculated by treating on- and off-peak consumption as two separate commodities, and applying the deadweight loss formula above (Equation F).

(F)	DWLUTOUpk  = 1/2 expk Upk [fpkon rpkon2+ fpkoff  rpkoff2]

where

DWLUTOUpk = unit deadweight loss ($/MWh) due to lack of TOU price signals, for demand level k, profile p

expk = cross-price elasticity of on-/off-peak consumption for demand level k, profile p

Upk = load weighted average annual price for ESIIDs in demand level k, profile p

Upkon = load weighted average price during on-peak periods only

Upkoff = load weighted average price during of-peak periods only

fpkon = fraction of energy during on peak periods only

fpkoff = fraction of energy during off peak periods only

= 1-fpkon

rpkon = relative difference between on-peak and annual average price

= (Upkon – Upk)/Upk

rpkoff = relative difference between off-peak and annual average price

= (Upkoff – Upk)/Upk

In principle, we could consider separate average on-peak, off-peak, and annual prices for each ESIID j.  As a simplification, we use the prices for the demand-profile bin kp as a whole.

This unit deadweight loss applies only to ESIIDs that are not already on TOU profiles.

## Overall Economic Costs

The two components of deadweight loss can be combined to give a total deadweight loss related to lack of interval metering.  Lowering the interval metering threshold eliminates this source of economic cost from the group of ESIIDs that would move from nonIDR to IDR as a result of the lowered threshold.  Conversely, increasing the threshold would increase this societal cost.

This societal benefit or cost related to the change in economic efficiency of the retail electric market can then be compared with the associated increase or decrease in metering costs.  While rules vary among TDSPs as to how these metering costs are paid for, the economic efficiency analysis does not depend on how these costs are assigned.  If metering is viewed as a means to provide appropriate price signals, the question is whether the value to the economy of improving those price signals outweighs the cost to the economy of installing additional metering.

It must be recognized that advanced metering can provide benefits beyond improved price signals.  These benefits include the potential for automated meter reading, as well as two-way communications.  A more complete analysis would consider the value of these additional benefits.

# APPENDIX B

Price Elasticity Assumptions for Dead Weight Loss Calculations

King (2003) reported bundled price elasticities as shown in the following table.

| Bundled price elasticities |  |  |  |
| --- | --- | --- | --- |
| Customer Type | Own-price Elasticity |  | Elasticity of Substitution |
|  | Short Run | Long Run |  |
| All | 0.175 | 0.407 | 0.150 |
| Commercial | 0.129 | 0.250 | 0.072 |
| Industrial | 0.068 | 0.157 | 0.053 |
| Residential | 0.260 | 0.605 | 0.145 |

For ERCOT’s analysis, we are unable to identify ESI IDs by customer type, commercial or business; as a result, an average non-residential elasticity is computed by averaging the commercial and industrial long run elasticities reported above.  Thus the resulting bundled price elasticity is estimated to be 0.204.

As indicated, the elasticties reported above are based on analysis of response to bundled prices; the non-TDSP component, which is the only component subject to ERCOT settlement, was assumed to represent 60% of the bundled price.  Thus the elasticity estimate used for the Dead Weight Loss calculation, was 0.60 × 0.204 = 0.122.

APPENDIX C

Tables for the Impact of Establishing a Demand Threshold Below Which IDRs Could Voluntarily Be Removed Analysis

# APPENDIX D

Tables for the Mandatory IDR Installation Threshold Analysis

# APPENDIX E

Tables for the Combination Mandatory Installation and Optional Removal Analysis

Reference the ERCOT Decision Tree at http://www.ercot.com/participants/loadprofiling.htm.

Reference ERCOT Protocols section 11 “Data Acquisition and Aggregation.”

Tariff information obtained from the PUCT website http://www.puc.state.tx.us/electric/rates/index.cfm section “Transmission and Distribution Rates for Investor Owned Utilities”.  ERCOT only considered metering charges and transmission system charges. For the purposes of this analysis ERCOT did not consider charges associated with service at transmission voltage or with secondary service less than 10 kW.

Provided by Kema-Xenergy, Inc.

The minimum length of time for an outage to qualify as a “sustained outage” varies from utility to utility.  For example, NSTAR Electric defines it as an outage longer than one minute, PG&E defines it as any outage longer than two minutes, and Detroit Edison defines it as outages that “usually last more than five minutes.” Bishop, McCarthy, and Rose (1998) did not define the term in their analysis.