## ERCOT Operations Report

## ROS & OWG

## December 2003

December-Frequency Control Issues (High or Low) 59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 12/11/2003 6:07 | 59.870 | 36034 | -271 | -1522 | 2650 (675) |
| 12/12/2003 17:02 | 60.102 | 33172 | -735 | 216 | 965 (910) |
| 12/12/2003 17:24 | 59.899 | 34163 | -768 | -117 | 171 MW resource lost |
| 12/12/2003 17:52 | 60.115 | 35112 | -1155 | -154 | VDI issued: reduce 300 MW |
| 12/14/2003 6:02 | 60.101 | 32350 | -1217 | 1349 | 1285 (400) |
| 12/22/2003 11:06 | 60.137 | 29333 | -128 | 930 | -410 (-1100) VDI issued: reduce 300 MW |
| 12/24/2003 22:02 | 59.895 | 28123 | 797 | -1222 | -2400 (-1300) |
| 12/26/2003 6:05 | 60.157 | 24365 | -1025 | 2623 | 2650 (375) |
| 12/26/2003 6:18 | 59.896 | 24324 | -860 | -290 | Offset (detailed below) |

| Time | Frequency |  |
| --- | --- | --- |
| 12/6/2003 1:30 | 59.825 | 560 MW Resource lost. |
| 12/6/2003 22:37 | 59.819 | 620 MW Resource lost. |
| 12/10/2003 8:55 | 59.859 | 450 MW Resource lost. |
| 12/12/2003 15:12 | 59.833 | 650 MW Resource lost. |
| 12/14/2003 3:45 | 59.877 | 450 MW Resource lost. |
| 12/14/2003 12:21 | 59.850 | 560 MW Resource lost. |
| 12/22/2003 8:28 | 59.698 | 1150 MW Resource lost. |
| 12/22/2003 8:41 | 60.105 | Overshoot recovering from trip. |

December -Locations and Relative Activity Capacity Purchases for OOMC & RMR

December Locations and Relative Activity of Congestion Management

Occurrences for December of 1 day or less, listed below:

Allen – P Tennyson				MGSES - Sweetwater Downtown Tap

Austrop – Lost Pines				Midland - Odessa

Austrop – Sandow				N McCallen – N Edinburg

Clearsprings - Zorn - Marion			Roanoke - Parker

DFW Autos					Sherry - Everman

Duke – N Edinburg				South - Houston

Eskota Sw – Sweetwater Downtown Tap	Spunky - Hood

Forney - Elkton				Tricorner – SCSES – Mt Enterprise

Forney – Royse Sw				Watermill – Cedar Hill

Lon Hill – Coleto Creek			Watermill – Tricorner - Trinidad

Menard – Gillespie				West Levee Auto

*Days of units purchased for some time in the area described.  Data taken from daily reports and is approximated for global overview purposes only.

New Procedures/ Forms/ Operations Bulletins

| Day-Ahead Desk V2R13 | 12/2/2003 | Incorporated TCN#64 into procedure; step 2.5 Priority Outage is a new section |
| --- | --- | --- |
| Transmission & Security Desk V2R15 | 12/2/2003 | Added new step to 2.2.2 regarding OOME offline |

# Security Alert Stage/ Threatcon/ Related issues

Security Threat Alert Yellow (Elevated) through December 21st.

Security Threat Alert changed to Orange (High) on December 21st at 12:30 PM by Dept Homeland Security.  ERCOT raised Threatcon level to modified Orange.

OCN, Advisory, Alert, Emergency Notice and Major Events

12/08              17:25 -21:30 Advisory issued for North – Houston.

12/18              10:15-12:15 Advisory issued for North – Houston.

Significant Communication Problems

12/14	Held 05:30 balancing deployments due to MOI down.

12/16	SBC fiber outage 09:50-12:45 - voice circuits to Taylor knocked out.

12/26	Held 06:00-06:15 balancing deployments.

12/30	Major phone problem outside of Taylor, Disaster Recovery Plan started.

## Major Computer Systems Problems/ Fixes

None.

# Major system Voltage problems

None.

Blackout/Load Shed incidents

12/22 08:28   approximately 425 MW of interruptibles tripped.

ERCOT peak (Unofficial)

12/17/03  40,329 MW

## Update on New Generation

No new generation made commercially available in the month of December.

## Max  Temperatures

Max:	12/01/03 – 77.5 degrees at the Far West.

# New SPS & RAP’s

None.

Other

12/10	Switched to Primary Site to Austin from 17:30 thru 23:30.

12/1 00:00  Adjusted minimum threshold for deployment of responsive reserve from 59.9 to 59.91