## ERCOT Operations Report

## ROS & OWG

## January 2004

Frequency Control Issues (High or Low) 59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 1/6/2004 22:03 | 59.899 | 38787 | 329 | -1067 | -3225( -1175) |
| 1/7/2004 22:04 | 59.887 | 35186 | 179 | -1434 | -3975(-1500) |
| 1/9/2004 6:08 | 59.898 | 31610 | 385 | -593 | 2600 (650) |
| 1/18/2004 6:05 | 60.101 | 24387 | -509 | 893 | 1675 (400) |
| 1/20/2004 6:02 | 59.889 | 37391 | 835 | -792 | 2625 (600) |
| 1/22/2004 22:04 | 59.899 | 30249 | -386 | -119 | -3950 (-975) |
| 1/23/2004 22:02 | 59.883 | 27775 | 495 | -849 | -3275 (-900) |
| 1/26/2004 0:11 | 60.115 | 22846 | -6 | 294 | Overshoot recovering from low frequency after 00:00 and change in steel mill load |
| 1/26/2004 4:49 | 60.106 | 23457 | 86 | 234 |  |
| 1/26/2004 18:10 | 59.892 | 34821 | 334 | -1160 |  |
| 1/27/2004 5:50 | 60.108 | 36858 | -573 | -209 | 2600 (600) |
| 1/27/2004 6:11 | 59.893 | 39007 | 187 | -998 | 2600 (600) |
| 1/27/2004 6:25 | 59.883 | 40184 | 1320 | -1431 | n/a |
| 1/30/2004 6:07 | 59.895 | 31957 | 1138 | -1038 | 4650 (1225) |
| 1/30/2004 12:34 | 59.897 | 32387 | 194 | -262 |  |
| 1/30/2004 14:20 | 60.108 | 30788 | -351 | 217 |  |

| Time | Frequency | Resource lost |
| --- | --- | --- |
| 1/4/2004 17:37 | 59.800 | 795 MW lost. Multiple resources tripped at the same station. |
| 1/5/2004 9:01 | 59.870 | 620 MW lost. Multiple resources tripped at the same station. |
| 1/5/2004 11:36 | 60.113 | corresponds with resources lost at 09:00 returning to service |
| 1/17/2004 23:48 | 59.845 | Resource ran back and recovered within seconds. MW output dropped from 700 to 300 and recovered to 650 MW. |
| 1/17/2004 23:50 | 60.102 | Overshoot from above |
| 1/18/2004 21:05 | 59.797 | 750 MW resource lost. 170 MW interruptible actuated. |
| 1/23/2004 16:16 | 59.680 | 1200+ MW Unit Trip 685 MW Interruptible actuated. |
| 1/24/2004 12:32 | 59.806 | 500 MW resource lost. 170 MW interruptible actuated |
| 1/25/2004 2:39 | 59.877 | 550 MW runback and trip. |
| 1/28/2004 11:52 | 59.880 | 450 MW resource lost. |
| 1/31/2004 22:32 | 59.813 | 725 MW resource lost. 170 MW interruptible actuated. |

January -Locations and Relative Activity Capacity Purchases for OOMC & RMR

January Locations and Relative Activity of Congestion Management

Post-Contingency Violation occurrences for January of 1 day listed below:

Allen SW-Renner-PTennyson			Miller - Weatherford

Big Brown-Venus				Morgan-Odessa

CPSES - DCSES – WHSES			North-Houston

Graham-Abilene-Sweetwater			Odessa-Moss Sw

Lon Hill-Whitepoint				Shamberger-Royse Sw

Lytton-Zorn

Midland - Odessa

Base Case Violation Occurrences for January listed below:

Big Foot XFMR

Lopeno-Falcon

OKLA-SW Vernon

Rio Pecos XFMR

*Days of units purchased for some time in the area described.  Data taken from daily reports and is approximated for global overview purposes only.

New Procedures/ Forms/ Operations Bulletins

| ERCOT Power Operations Bulletin 59 | 01/08/2004 | Verbal Dispatch Exception (Temporary Work Around)– Frequency Control Desk |
| --- | --- | --- |
| ERCOT Power Operations Bulletin 60 | 01/08/2004 | Verbal Dispatch Exception (Temporary Work Around)– Transmission & Security Desk |
| ERCOT Power Operations Bulletin 61 | 01/21/2004 | Revision to Shift Supervisor section – Operations Procedure Manual (Procedure To Allow Unit Testing when Constraints Are Active) |
| ERCOT Power Operations Bulletin 62 | 01/23/2004 | Procedure to Verify the Daily Dynamic Ratings Update (Pilot Program) – Temporary Change for Transmission & Security Desk (Scheduled to Expire on March 26, 2004) |
| ERCOT Power Operations Bulletin 63 | 01/26/2004 | Revision to Shift Supervisor Desk |

# Security Alert Stage/ Threatcon/ Related issues

Security Threat Alert Orange (High) through January 9th 11:00 AM.

Security Threat Alert lowered to Yellow (Elevated) on January 9th at 11:00 AM in response to Homeland Security and the DOE change of status from Orange to Yellow.

OCN, Advisory, Alert, Emergency Notice and Major Events

01/06   Weather Advisory issued for freezing temperatures and gas curtailments

01/06   Weather Advisory issued for freezing temperatures and gas curtailments 00:00 – 12:00.

01/26	Issued OCN at 18:00 due to gas curtailments and freezing weather.  This was extended and effective through January 30th.

01/26 	20:20 – 24:00 Transmission Alert due to West Levee #2 above limit.

01/27	07:40 – 13:30 Transmission Alert issued for Lopeno – Falcon 138 kV.

01/28	06:30 – 23:00 Transmission Alert issued for Lopeno – Falcon 138 kV.

01/29	07:40 – 23:00 Transmission Alert issued for Lopeno – Falcon 138 kV.

Significant Communication Problems

01/01	Balancing Energy market held due to year end zone changes.  	00:00-00:15

01/07	Portal down from 19:00-19:55.

01/15	Held 07:30-08:00 deployments due to MOI being down.  A process error caused the database to stop.

## Major Computer Systems Problems/ Fixes

01/04	MOI, EMS, and Portal down in Taylor from 09:15-10:15 due to maintenance error.

# Major system Voltage problems

None.

Blackout/Load Shed incidents

1/18/2004 21:05   	170 MW interruptible actuated.

1/23/2004 16:16	685 MW interruptible actuated.

1/24/2004 12:32	170 MW interruptible actuated.

1/31/2004 22:32	170 MW interruptible actuated.

ERCOT peak (Unofficial)

01/06/04   42,288 MW

## Update on New Generation

No new generation approved for synchronization in the month of January.

## Max Temperature

01/02/04 – 82.0 (South)

# New SPS & RAP’s

None.

Other

Maximum LaaR threshold for RRS remained 50%