# SPWG Report to ROS

#### April 13th, 2004

SPWG last met February 26th and 27th, 2004.

SPWG member companies have been requested to review zone 3 relay settings (i.e. longest reaching phase distance element that will cause tripping in either direction) on lines rated 345 kV and above to determine compliance with NERC recommendations. Review must be completed by September 30, 2004.

Updated underfrequency relay spreadsheet data was due to Mark Henry on April 1, 2004. Data to include underfrequency relay information on a per bus basis (bus number used in the ERCOT short circuit case).

Non-LaaR industrial load tripped during the May 15th, 2004, underfrequency event was due to Mark Henry on April 1, 2004.

Future year (2005-2008) short circuit cases are due to Woody Rickerson, ERCOT, by April 15, 2004. Data should be submitted in PSSE version 29 format.

SPWG members have agreed that the present work environment better supports compilation of the future short circuit databases starting in April rather than late summer. SPWG Procedures will be modified to reflect the revised schedule, reviewed by SPWG members and should be ready for ROS consideration at the May ROS meeting.

SPWG members are reviewing a draft document on system protection maintenance plan requirements in another NERC region (NPCC).  Members will forward comments to Mark Henry.  Further discussion/action will take place at the SPWG meeting in July.

Disturbance monitoring equipment location criteria presently applies to equipment operated at 60 kV or above. This is a change from wording previously approved by the SPWG specifying 100 kV and above. SPWG members agreed reference to 60 kV should be revised to 100 kV. An OGRR will be prepared.

Next SPWG meeting is scheduled for July 29th and 30th, 2004, in Taylor, Texas.

Jack Dahnke

SPWG Chair