## ERCOT Operations Report

## ROS & OWG

## March 2004

March-Frequency Control Issues (High or Low) 59.9 > F > 60.1

|  | C POINT | MW LOST | A POINT |
| --- | --- | --- | --- |
| 3/3/2004 15:07 | 59.833 | 770 | 60.068 |
| 3/3/2004 15:58 | 59.897 | 156 + 144 AT STATION | 59.959 |
| 3/4/2004 12:30 | 59.861 | 370 | 59.936 |
| 3/10/2004 19:12 | 59.890 | 335 | 59.976 |
| 3/11/2004 3:04 | 59.820 | 510 | 59.954 |
| 3/12/2004 13:17 | 59.824 | 395 | 59.66 |
| 3/12/2004 16:10 | 59.880 | 194+106 AT STATION | 59.932 |
| 3/13/2004 16:08 | 59.880 | 355 | 60 |
| 3/16/2004 13:44 | 59.897 | 160 + 81 AT STATION | 59.97 |
| 3/16/2004 21:45 | 59.897 | 128 + 72 AT STATION | 59.948 |
| 3/18/2004 12:43 | 59.882 | 660 | 59.98 |
| 3/18/2004 15:27 | 59.869 | 320 | 59.941 |
| 3/26/2004 9:27 | 59.818 | 600 | 60.02 |
| 3/26/2004 9:37 | 60.101 | Overshoot recovering from trip |  |
| 3/30/2004 12:58 | 59.889 | 450 | 59.995 |
| 3/31/2004 17:31 | 59.834 | 415 | 59.935 |

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 3/1/2004 6:04 | 59.875 | 28045 | -71 | -382 | 4282 (860) |
| 3/1/2004 22:08 | 60.113 | 27403 | -1031 | 502 | -2800 (-750) |
| 3/2/2004 22:15 | 60.126 | 28130 | -303 | 512 | -3850 (-1000) |
| 3/4/2004 6:49 | 60.103 | 28653 | 146 | 305 | Steel mill activity and QSE Gen telemetry problems |
| 3/5/2004 16:04 | 60.113 | 28931 | -326 | -899 |  |
| 3/7/2004 9:06 | 60.139 | 24744 | -956 | 81 | 650 (440) |
| 3/10/2004 18:03 | 60.118 | 28377 | -414 | 450 |  |
| 3/12/2004 22:16 | 60.141 | 27135 | -541 | -164 | -2525(-850) |
| 3/17/2004 5:58 | 60.112 | 24930 | -484 | 412 | 3550 (1265) |
| 3/18/2004 6:02 | 60.146 | 24905 | -765 | 794 | 2890 (1030) |
| 3/22/2004 6:07 | 59.897 | 25538 | 845 | -687 | 3715 (1150) |
| 3/22/2004 6:43 | 60.101 | 27273 | 1038 | 13 | Overshoot recovering from low frequency at 06:41 |
| 3/23/2004 1:04 | 60.113 | 21846 | -236 | 254 | Steel mill activity |
| 3/23/2004 5:32 | 60.111 | 23738 | -386 | 203 |  |
| 3/28/2004 12:34 | 60.133 | 29380 | -95 | -456 |  |
| 3/29/2004 0:07 | 59.898 | 23387 | -139 | -281 | 1675 (400) |
| 3/30/2004 23:47 | 60.101 | 23198 | 120 | 373 | Steel mill activity |

Responsive Deployed at: (Listed Above)

| 01-Mar-04 05:01:00 | 06-Mar-04 09:01:00 | 19-Mar-04 06:12:00 |
| --- | --- | --- |
| 01-Mar-04 06:12:00 | 07-Mar-04 12:04:00 | 20-Mar-04 15:10:00 |
| 01-Mar-04 18:19:00 | 10-Mar-04 18:38:00 | 22-Mar-04 06:05:00 |
| 01-Mar-04 20:04:00 | 10-Mar-04 19:11:00 | 23-Mar-04 06:05:00 |
| 02-Mar-04 06:06:00 | 11-Mar-04 03:04:00 | 23-Mar-04 08:02:00 |
| 02-Mar-04 08:05:00 | 12-Mar-04 13:17:00 | 24-Mar-04 00:00:00 |
| 03-Mar-04 10:01:00 | 12-Mar-04 16:10:00 | 25-Mar-04 06:04:00 |
| 03-Mar-04 15:07:00 | 13-Mar-04 16:08:00 | 26-Mar-04 09:27:00 |
| 03-Mar-04 15:58:00 | 16-Mar-04 13:44:00 | 28-Mar-04 12:09:00 |
| 04-Mar-04 06:11:00 | 16-Mar-04 14:22:00 | 29-Mar-04 00:06:00 |
| 04-Mar-04 12:30:00 | 16-Mar-04 21:45:00 | 30-Mar-04 07:05:00 |
| 05-Mar-04 06:05:00 | 18-Mar-04 12:41:00 | 30-Mar-04 12:58:00 |
| 05-Mar-04 07:09:00 | 18-Mar-04 14:00:00 | 31-Mar-04 11:44:00 |
| 05-Mar-04 10:20:00 | 18-Mar-04 15:27:00 | 31-Mar-04 17:35:00 |

February -Locations and Relative Activity Capacity Purchases for OOMC & RMR

| Historical | Mar-03 | Feb-04 | Mar-04 |
| --- | --- | --- | --- |
| DFW | 143 | 58 | 38 |
| E RIO | 51 | 49 | 46 |
| W RIO | 43 | 58 | 33 |
| Laredo | 39 | 29 | 25 |
| Rio Pecos | 31 | 0 | 0 |
| Corpus | 28 | 29 | 25 |
| Abilene | 8 | 36 | 62 |
| San Angelo | 5 | 27 | 19 |
| Western | 4 | 14 | 9 |
|  | 352 | 300 | 257 |

*Days of units purchased for some time in the area described.  Data taken from daily reports and is approximated for global overview purposes only.

March Locations and Relative Activity of Congestion Management (Unit-Days)

| Loss Of | Overloads | Count |
| --- | --- | --- |
| Tenaska TMPP - Concord 138kv | Lilian - Grandview TMPP 138kv | 25 |
| Clear Springs-Marion-Zorn | Cibolo-McQueeney | 15 |
| N Edin-Rio Hondo | Weslaco-N Weslaco | 6 |
| STP - WhitePoint 345 KV | Blessing -Lolita 138kv | 5 |
| N McAllen-N Edin | North Edinburg - Moore Field | 5 |
| N McAllen-N Edin | Polk - Hall Acres | 5 |
| Midland-Odessa | Odessa-Big Three Tap | 5 |
| Big Brown - Venus 345 kv | Cedar Hill - WaterMill 345kv | 5 |
| Greens Bayou – King Double 345 kV | Greens Bayou 345/138 | 5 |
| STP - WhitePoint 345 KV | Blessing - STP 138kv | 3 |
| Farmersville - Monticello 345kv | Paris Switch - Valley Switch 345kv | 3 |
| Farmersville - Monticello 345kv | Monticello - Paris Switch 345kv | 3 |
| Duke-N Edin | Duke-N Edin | 3 |
| Bates - Garza 138kv | Bates 138/69 KV | 3 |
| Asherton-Eagle Pass | Uvalde-Ashphalt Mines | 3 |
| N Edin-Rio Hondo | Duke-N Edin | 2 |
| Ingleside Dupont Switch - Oxygen Chem Gen 138kv | DU_DUPP1 138kv | 2 |
| Graham-Parker-Benbrook | Stephenville-Lingleville | 2 |
| Crane LCRA-Midkiff Sw | Crane TU-Humble | 2 |
| Abilene Mulberry - Oklaunion 345kv | Wichita Falls - Fisher Road 138kv | 2 |
| 138kv line Ennis Sw to Desoto Sw | Desoto Sw to S.Ennis | 2 |
| Abilene Elm Creek - Abilene Mulberry Creek 138kv | Abilene Elm Creek - Abilene Northwest 138kv | 2 |
| West Columbia Main - Angleton Ret 138kv | West Columbia Main - Texas Gulfsulphur 138kv | 1 |
| Sandow to Temple 345 kv | Copperas Cove to Killeen Ft Hood Sw | 1 |
| Sandow to Temple 345 kv | Sandow to Rogers | 1 |
| Sandow - Austrop 345kv | Sandow - Salty 138kv | 1 |
| N McAllen-N Edin | Duke-N Edin | 1 |
| Morgan-Odessa | General Tire Sw-Olefin Sw 138 KV | 1 |
| Graham-Sweetwater Cogen Swtich 345kv | Graham-Murray 138kv | 1 |
| Crane LCRA - North McCamey 138kv | Ft. Lancaster - Illinois 69kv | 1 |
| Comanche Peak-Parker Sw 345 | Bryant Irvin-Benbrook 138 Kv | 1 |
| Comache Peak-Decordova/Wolf Hollow-Rock Creek 345 | Comache Peak-Parker 345 | 1 |
| Clear Springs-Marion-Zorn | Structural Metals Inc. - McQueeny 138kv | 1 |
| Clear Springs-Marion-Zorn | Cico - Comfort 138kv | 1 |
| Big Lake - North McCamey 138kv | Illinois 4 - Fort Lancaster 69kv | 1 |
| Austrop-Sandow | Gilleland Creek-McNeil LCRA 138 | 1 |
| Abilene East - Fort Phantom 138kv | Abilene Elm Creek - Abilene Northwest 138kv | 1 |
| Abilene East - Fort Phantom 138kv | East Abilene - Abilene Northwest 69kv | 1 |
| Vernon-Oklaunion 138kv | Vernon - Sand 69kv | 1 |
| Palmview-Bates 138 | Bates-Misson 69kv | 1 |
| Ned-Magic Valley Coop 138 | Duke-N Edin | 1 |
| Jeanetta-White Oak 345 KV line | Garrot-Thermal Energy | 1 |
| George West - Sigmor Grove 138kv | Pleasant Transformer 138/69 | 1 |
| Angelton Reit-West Columbia 138 | Wharton-South Lane City 138 | 1 |

New Procedures/ Forms/ Operations Bulletins

Power Operations Bulletins 70 – 74

- (3/08)	Controlling renewable resources in the McCamey area in accordance with PRR 397.

- (3/08)	Clarification added to POB 70.

- (3/18)	Manual processes used for phase 1 of PRR 425 implementation (outage approval process).

- (3/18)	Clarification added to POB 70.

- (3/29)	TCN#96 -  Procedure for implementing TO provided dynamic ratings.

# Security Alert Stage/ Threatcon/ Related issues

Security Threat Alert Yellow (Elevated) maintained through March.

OCN, Advisory, Alert, Emergency Notice and Major Events

3/04 13:00 – 23:00 Weather Advisory for North and Central Texas.

3/04 14:25-23:00  Alert issued due to forced outage of Northeast – North CSC elements.

3/04 17:15 – 3/05 18:45  Emergency Notice for transmission in Northeast Texas due to multiple    forced transmission outages.

3/15   13:27   Emergency Notification posted for the outage of the East DC tie.

3/16   15:30-24:00  Transmission Alert.  North McAllen – North Edinberg and North Edinberg – Moore above first contingency limit.

3/29   23:30 – 00:15   Transmission Alert.  Loss of Oklaunion – Mulberry Creek 345 kV overloads Wichita Falls– Fisher Road 138 kV.

Significant Communication Problems

3/2  	14:15 – 15:15.  Held deployments.  Both SPD servers had crashed.

3/3  	10:15  Fail over populated incorrect short-term load forecast values.

3/5 	Held 01:30 interval.

3/13     19:02  Portal down for planned maintenance.

3/14	10:50  Portal down.

3/14	11:45 Portal down.

3/15	13:45	Extended market to 14:00 due to problems with the MOI.

3/15	03:15 – 03:45 Deployments sent via phone due to Portal not sending them.

3/16	Held 21:45 interval.  Deployments were not sent.

03/23   09:55 Planned site fail over.  MOI disabled 09:55-10:05, POS disabled 09:55-10:08, Portal disabled 10:00 – 10:50.

ERCOT peak (Unofficial)

03/18/04  20:00 34,259

## Update on New Generation

Deer Park Energy #4	185 MW	Harris County

Leon Creek CT1	 57 MW	Bexar County

## Max Temperature

3/19   90 F in Far West