## ERCOT Operations Report

## ROS & OWG

## April 2004

April-Frequency Control Issues (High or Low) 59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 4/5/2004 6:05 | 59.899 | 24434 | -432 | -169 | 3375 (1175) |
| 4/6/2004 6:05 | 59.894 | 25120 | -348 | -107 | 3900 (1125) |
| 4/9/2004 6:02 | 60.172 | 23272 | -809 | 675 | 3600 (1100) |
| 4/9/2004 22:01 | 59.891 | 30992 | 265 | -1112 | -1900 (-1915) |
| 4/9/2004 22:11 | 60.102 | 30723 | 262 | -85 | -1900 (-1915) |
| 4/10/2004 6:00 | 60.128 | 22561 | -663 | 1022 | 5580 (1410 |
| 4/11/2004 6:03 | 60.136 | 21412 | -92 | 741 | 1275 (1100) |
| 4/14/2004 5:02 | 59.897 | 23775 | -190 | -128 | 1740 (350) |
| 4/15/2004 0:30 | 60.137 | 22698 | 324 | 365 | n/a |
| 4/15/2004 2:17 | 60.120 | 21537 | -92 | 389 | n/a |
| 4/15/2004 2:41 | 60.120 | 21367 | -625 | 401 | Out of Down Reg 2:31-2:49 |
| 4/15/2004 16:04 | 60.102 | 31476 | -51 | 192 | Steel mill off line |
| 4/16/2004 5:46 | 60.110 | 23713 | 272 | 302 | 3800 (1175) |
| 4/16/2004 6:08 | 59.895 | 25358 | 269 | 213 | 3800 (1175) |
| 4/18/2004 6:01 | 60.167 | 22058 | -723 | 1175 | 1175 (1165) |
| 4/19/2004 6:05 | 59.884 | 26033 | -198 | -342 | 3650 (1215) |
| 4/19/2004 16:04 | 60.106 | 33913 | -324 | 311 | n/a |
| 4/20/2004 18:00 | 60.102 | 33225 | -357 | 41 | 1 QSE with incorrect SCE due to computer problem. Second with constraint recently released |
| 4/21/2004 5:30 | 60.116 | 24782 | 244 | 225 | Recalling Reg deployed from low frequency 05:14- 05:24 |
| 4/21/2004 21:55 | 60.100 | 34177 | -626 | 201 | -3175 (-720) |
| 4/22/2004 11:06 | 60.103 | 33942 | -454 | -105 | Calculated SCE -636 @ 11:01 |
| 4/24/2004 1:01 | 60.119 | 26258 | -153 | 666 | -1400 (-325) |
| 4/25/2004 22:14 | 60.123 | 29266 | -59 | 340 | -2225 (-700) |
| 4/26/2004 6:09 | 59.858 | 25594 | 1000 | -1250 | 2750 (1790) |
| 4/27/2004 6:05 | 59.896 | 24629 | 242 | -1242 | 3975 (775) |
| 4/27/2004 20:16 | 59.899 | 34570 | 809 | -1029 | n/a |
| 4/28/2004 6:00 | 60.125 | 24736 | -780 | 1223 | 4270 (840) |
| 4/28/2004 6:15 | 59.854 | 25872 | 70 | -373 | 4270 (840) |
| 4/29/2004 6:00 | 60.106 | 25380 | -541 | 465 | 40000 (800) |
| 4/29/2004 21:52 | 60.100 | 34495 | 211 | 119 | -3500 (-675) |

| Time | Frequency | MW LOST |
| --- | --- | --- |
| 4/2/2004 9:37 | 59.885 | 350 |
| 4/9/2004 12:47 | 59.788 | 825 Multiple Units, some runback |
| 4/23/2004 12:50 | 59.845 | 665 Multiple Units |
| 4/24/2004 19:11 | 59.852 | 640 |
| 4/24/2004 19:50 | 59.893 | 275 Multiple Units |
| 4/27/2004 0:30 | 59.884 | 250 |
| 4/29/2004 23:12 | 59.899 | 450 |
| 4/30/2004 2:02 | 59.899 | 210 |
| 4/30/2004 2:45 | 59.889 | 550 Multiple Units |

Responsive Deployed at: (Listed Above)

| 01-Apr-04 06:09:00 |  | 19-Apr-04 07:12:00 |  | 09-Apr-04 21:57:00 |
| --- | --- | --- | --- | --- |
| 05-Apr-04 06:03:00 |  | 12-Apr-04 08:03:00 |  | 10-Apr-04 21:57:00 |
| 06-Apr-04 06:03:00 |  | 21-Apr-04 08:00:00 |  | 15-Apr-04 21:57:00 |
| 07-Apr-04 06:03:00 |  | 02-Apr-04 09:36:00 |  | 17-Apr-04 21:57:00 |
| 08-Apr-04 06:03:00 |  | 13-Apr-04 11:03:00 |  | 09-Apr-04 22:00:00 |
| 10-Apr-04 06:06:00 |  | 09-Apr-04 12:45:00 |  | 25-Apr-04 22:00:00 |
| 13-Apr-04 06:03:00 |  | 23-Apr-04 12:48:00 |  | 15-Apr-04 23:00:00 |
| 14-Apr-04 06:03:00 |  | 14-Apr-04 13:54:00 |  | 21-Apr-04 23:00:00 |
| 16-Apr-04 06:03:00 |  | 07-Apr-04 14:15:00 |  | 29-Apr-04 23:11:00 |
| 19-Apr-04 06:03:00 |  | 02-Apr-04 15:24:00 |  | 11-Apr-04 00:00:00 |
| 21-Apr-04 06:09:00 |  | 09-Apr-04 15:54:00 |  | 15-Apr-04 00:00:00 |
| 22-Apr-04 06:06:00 |  | 26-Apr-04 16:09:00 |  | 30-Apr-04 00:02:00 |
| 23-Apr-04 06:03:00 |  | 27-Apr-04 16:23:00 |  | 27-Apr-04 00:32:00 |
| 26-Apr-04 06:03:00 |  | 24-Apr-04 19:09:00 |  | 22-Apr-04 01:00:00 |
| 27-Apr-04 06:03:00 |  | 24-Apr-04 19:48:00 |  | 18-Apr-04 02:48:00 |
| 28-Apr-04 06:17:00 |  | 25-Apr-04 19:48:00 |  | 30-Apr-04 02:02:00 |
| 30-Apr-04 06:08:00 |  | 22-Apr-04 20:00:00 |  | 30-Apr-04 02:44:00 |
|  |  | 27-Apr-04 20:28:00 |  | 14-Apr-04 05:00:00 |
|  |  |  |  | 16-Apr-04 05:00:00 |

February -Locations and Relative Activity Capacity Purchases for OOMC & RMR

| Historical | 3-Apr | 4-Mar | 4-Apr |
| --- | --- | --- | --- |
| DFW | 130 | 38 | 77 |
| E RIO | 56 | 46 | 48 |
| W RIO | 20 | 33 | 6 |
| Laredo | 33 | 25 | 47 |
| Rio Pecos | 30 | 0 | 0 |
| Corpus | 30 | 25 | 27 |
| Abilene | 3 | 62 | 41 |
| San Angelo | 18 | 19 | 30 |
| Western | 4 | 9 | 6 |
| Houston | 6 | 0 | 1 |
| San Antonio | 0 | 0 | 19 |
|  | 330 | 257 | 302 |

April Locations and Relative Activity of Congestion Management (Days)

| Contingency | Overload | Occurrences |
| --- | --- | --- |
| Lon Hill Whitepoint | Nueces Bay - Whitepoint | 12 |
| Northeast - North CSC |  | 11 |
| Duke - Pharr | Duke - N. Edinburg | 8 |
| Marion - Hill Country/ Skyline | Cibolo - Schertz | 8 |
| Monticello - Allen/Royse | Allen - Ben Davis | 7 |
| Temple - Lake Creek/Tradinghouse | Temple - Lake Creek | 7 |
| North - Houston CSC |  | 4 |
| South to Houston CSC |  | 4 |
| Big Brown - Venus | Watermill - Cedar Hill | 3 |
| Big Lake - N McCamey | Ft Lancaster - Illinois | 3 |
| Comanche Peak -Decordova/ Wolf Hollow-Rocky Creek | Spunky - Hood | 3 |
| Duke - N. Edinburg | Duke - N. Edinburg | 3 |
| Monticello - Allen/Royse | Tricorner - Watermill | 3 |
| N McCallen - Nedin | Polk - Hall Acres | 3 |
| Pawnee - Calaveras | Leon Creek - Pleasanton | 3 |
| Rion Hondo - La Palma | Weslaco - N Weslaco | 3 |
| Austrop - Zorn | Flatonia - Halletsville | 2 |
| Bates - Garza | Bates Auto | 2 |
| Bowman - Graham | Fisher Road - Wichita | 2 |
| Carrolton NW Transformer | N Parkway - Renner | 2 |
| Enterprise - Martin Lake/Trinidad - Stryker Creek | Nacogdoches 345/138 | 2 |
| Sandow -Austrop | Austrop Auto | 2 |
| Stryker Creek - Trinidad | Martin Lake - Tricorner | 2 |
| Temple - Lake Creek/Tradinghouse | Ballinger - Paint Rock | 2 |
| Tricorner -Watermill/Trinidad | Seagoville - Kleberg Tap | 2 |
| Benbrook - Comanche Peak | Bryant Irvin - Wedgewood | 1 |
| Benbrook - Comanche Peak | Benbrook - Bryan Irvin | 1 |
| Benbrook - Decordova | Benbrook - Bryan Irvin | 1 |
| Big Brown - Richland Chambers | Tricorner - Watermill | 1 |
| Carrolton NW Transformer | Tricorner - Watermill | 1 |
| Clear Spring-Marion-Zorn | McQueeney - SMI | 1 |
| Comanche Peak - Wolf Hollow | Bryant Irvin - Wedgewood | 1 |
| Crane - Midkiff | Crane - Humble | 1 |
| Duke - N. Edinburg | Polk - Hall Acres | 1 |
| Farmersville - Valley | Valley 345/138 | 1 |
| Farmersville -Monticello | Monticello - S Springs | 1 |
| Friend Ranch - Big Lake | Friend Ranch - Ozona | 1 |
| Frontera - N McCallen | Frontera - S McCallen | 1 |
| Gibbons Creek - Obrien | Hearne - Branchville | 1 |
| Henne - Comal | Zorn - Seguin | 1 |
| Holly - Airport | Holly- B Davis | 1 |
| Lytton Springs - Zorn/Austrop Zorn | Flatonia 138/69 | 1 |
| McCallen - Frontera | Bates Auto | 1 |
| Monticello - Allen/Sulpher Springs | Royse - Farmersville | 1 |
| Morgan Creek - Odessa | Odessa - Big Three | 1 |
| Morgan Creek - Odessa | Ballinger - Paint Rock | 1 |
| Pawnee - Calaveras | Leon Creek - Howard Road | 1 |
| Pleasanton - Moore | Pleasanton Transformer | 1 |
| Renner - North Lake | NW Carrollton Transformer | 1 |
| Royse Forney | Tricorner - Watermill | 1 |
| San Angelo -Menard | Ballinger - Paint Rock | 1 |
| South-North CSC |  | 1 |
| STP - Whitepoint | Blessing - Lolita | 1 |
| Tradinghouse - Venus | Grandview - Whitney | 1 |

New Procedures/ Forms/ Operations Bulletins

Power Operations Bulletins 75 – 81

- Hotline Call for Portal Outages longer than 15 minutes. (Supervisor)

- Added guidance for creating an estimated end time for a forced outage and updated language for PRR 425.  (Transmission)

- (TC)  Allows for approved outages to be temporarily interrupted. (Transmission)

- Coordinating rating changes and monitoring CSC limits. (Supervisor)

- Coordinating rating changes and monitoring CSC limits. (Transmission)

- (TC)  OOME off line instructions for combined cycle units. (Transmission)

# Security Alert Stage/ Threatcon/ Related issues

Security Threat Alert Yellow (Elevated) maintained through April.

OCN, Advisory, Alert, Emergency Notice and Major Events

4/1  14:57   Transmission Alert for  Leon Creek – Pleasanton.

4/6  12:00-17:00  OCN issued for severe weather in the Coast Zone

4/15 14:35  Transmission Alert for Lake Creek – Temple.

4/21  06:55 Transmission Alert for North Parkway – Renner.

4/26 16:03  Transmission Alert for Ben Davis – Allen Switch.

4/29 11:30  Transmission Alert for Flatonia 13/69 kV Transformer.

4/30 16:50  Transmission Alert for Ben Davis – Allen Switch.

ERCOT peak (Unofficial)

4/22 17:00	39,090

## Max Temperature

4/22	93 F 	Far West