## Assignments
June 2004 Summary of ERCOT Actions Related to NERC Board Recommendations on Blackout
Rec. # | Short Description | Responsibility |  | ERCOT Group | Comments (updates in italics)
|  | ERCOT? | Other's)?
1.a | FE, MISO, and PJM shall complete remedial action plan | N/A | FE/MISO/PJM
1.b | NERC to assist in 1.a | N/A | NERC
2.a | Significant Violations/ Quarterly Violations Reporting | X |  | Compliance | NERC Board approved interim guidelines. Monthly reporting of 7 "significant" operating templates will start in May. Monthly and quarterly reporting forms are developed and will be completed by Compliance.
2.b | Violation Corrective Actions | X |  | Compliance | Details are lacking, but this should not create additional requirements.
2.c | Compliance Templates | X | NERC CTTF | Compliance | NERC Board has approved 37 templates for 2004, mostly revisions to existing measures. Need to review for additional impact on ERCOT; possible Guides changes. These will be assessed beginning June 2004, replacing those measures previously in the NERC program
2.d | Evaluation identified violations | N/A | ECAR/NERC |  | Mark Henry assigned to Compliance Mgr task force on this.
3.a | Readiness Audit Program |  | NERC |  | ERCOT itself performs the Control Area & Reliability Coordinator functions and will be audited in 2004.
3.b | Audit Criteria |  | NERC |  | Audits are ongoing and are similar to old ERCOT processes from the early 1990's. RC audit criteria in draft.
3.c | Readiness Audits | X | NERC | ERCOT Operations | NERC will likely assemble a team for the ERCOT audit in the second half of 2004.
4.a | Vegetation Related Outage Reporting Program | X | NERC | 345kV Transmission Owners | A NERC compliance measure has been approved, monthly reporting from TO's with 345kV lines retroactive to Jan 1, 2004, and vegetation management plan self-certifications and audits. Part of letter sent to transmission companies.
4.b | Vegetation Related Outages Annual Report | X | Transmission Operators | 345 kV Transmission Owners | ERCOT must request transmission companies to complete this for 2004, data for first six months of 2004 due July 20th, and the 20th of each month thereafter..
4.c | Vegetation Management Procedures | X | Transmission Owners | 345 kV Transmission Owners | ERCOT transmission companies will need to assemble these documents. Need OWG to assist.
5.a | Recommendations Actions Tracking Program | X | NERC | Compliance/ROS | The ERCOT significant event investigation process was developed last Fall and includes provisions to track events from inside ERCOT. NERC to develop additional process.
5.b | NERC Reliability Monitoring Function |  | NERC |  | Not established what this entails. Certain compliance measures assess operational performance and will likely be the basis for this function.
6 | Operators Training | X | Control Areas, Rel. Coord. | Transmission Operators and ERCOT Operations | This applies to ERCOT and its transmission operators, but its not clear it should include smaller TO's in ERCOT. All 345kv Owners either met or expect to meet this recommendation by June 30.
7.a | Reactive & Voltage Standards Evaluation |  | NERC PC |  | This may result in future requirements, but ERCOT's Planning Committee representative will have to keep the Region informed.
7.b | ECAR Review | N/A | ECAR
8.a | Zone 3 Relay Review/Analysis | X | Transmission Owners | SPWG/345 kV line owners | ERCOT 345kV transmission must perform this review by Sept. 30. All TO's indicate they have or will complete this.
8.b | UVLS Studies | X | Transmission Owners | ROS | ROS asked Compliance to work with ERCOT Planning on this task, Ken Donohoo has agreed to help with recommendations by Sept. Some TO's have addressed this and are planning additions.
8.c | Planning Standard III evaluation |  | NERC PC |  | This may result in future requirements, but ERCOT's Planning Committee representative will have to keep the Region informed.
9 | Operating Committee Policies & Procedures Evaluation |  | NERC OC |  | This may result in future requirements, but ERCOT's Operating Committee representative will have to keep the Region informed. Revisions of Policy 4,5,6 & 9 underway.
10 | Operating Committee Real Time Tool Evaluation |  | NERC OC |  | This may result in future requirements, but ERCOT's Operating Committee representative will have to keep the Region informed.
11.a | August 14 System Restoration Evaluation |  | NERC PC/OC; PJM; NPCC, ECAR |  | N/A to ERCOT except for the Planning and Operating Committee representatives.
11.b | Blackstart & Restoration Evaluation | X |  | ROS | No information yet on dates. ERCOT will need to review these after release.
12.a | Regional Criteria for Synchronized Recording Devices | X |  | SPWG | ROS assigned SPWG to review Operating Guides to define locations that need time synchronization and evaluate whether enough time synced equipment is installed.
12.b | Dynamic Recorder Upgrade/Installation | X | Facilities Owners | SPWG/DWG | May require ERCOT companies to install equipment to allow for time synchronization and possibly dynamic data recorders. ROS assigned DWG to provide recommendation for ERCOT; initial discussion with DWG members in May.
13.a | Operating Committee Evaluation of Operations Planning & Operating Criteria |  | NERC OC |  | It is unclear what Operation Planning & Criteria will be evaluated by the NERC OC - could this involve the regions?
13.b | ECAR Study & Practices Reevaluation | N/A | ECAR |  | This may result in future requirements, but ERCOT's Operating Committee representative will have to keep the Region informed.
13.c | Evaluation of Planning Processes |  | NERC PC |  | This may result in future requirements, but ERCOT's Planning Committee representative will have to keep the Region informed. ROS may want to assign review of NERC recommendations or suggestions to SSWG or DWG.
14 | Model Data Validation | X |  | DWG | ROS assigned DWG to define what should be done here for modeling data and simulations, beyond any current validation. ERCOT lacks specific requirements to compare models with actual system performance. DWG held brief discussion in May.
Note on A6: Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthermore, each organization shall present its detailed plan for completing these actions to the NERC committees for technical review on March 23-24, 2004, and to the NERC board for approval no later than April 2, 2004.
Note on A7: Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity may seek technical assistance.
Note on A8: Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant1 violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards.
Note on A9: Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico.
Note on A10: Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
Note on A11: Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
Note on A12: Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004.
Note on A13: Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators.
Note on A14: Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams.
Note on A15: Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system3 transmission line trips resulting from vegetation contact4. The program will use the successful WECC vegetation monitoring program as a model.
Note on A16: Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004.
Note on A17: Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency.
Note on A18: Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board.
Note on A19: Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
Note on A20: Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations5, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits.
Note on A21: Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed.
Note on A22: Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
Note on A23: Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system.
Note on A24: Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system.
Note on A25: Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
Note on A26: Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
Note on A27: Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
Note on A28: Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
Note on A29: Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region.
Note on A30: Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances.
Note on A31: Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders.
Note on A32: Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
Note on A33: Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
Note on A34: Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information.
Note on A35: Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation.

## Summary
ERCOT (Summary) Tasks Related to NERC Board Recommendations on Blackout Status - Initial Draft April 7, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Further
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthermore, each organization shall present its detailed plan for completing these actions to NERC committees for technical review on March 23-24, 2004, and to the NERC board for approval no later than April 2, 2004. | 2004-06-30 | N/A ERCOT
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity may seek technical assistance. |  | N/A ERCOT
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | ERCOT Compliance currently reports on frequency control and transmission security violations on a monthly basis, or can without significant additional effort. Quarterly reports to the NERC Board started in 2003. Additional information may need to be added to this reporting, which does not presently address all NERC measures and addresses no ERCOT-specific standards.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | This suggests that NERC's Board will assist enforcement and mitigation of non-compliance. Details are lacking, but unless NERC makes demands beyond those determined by ERCOT in its compliance process for mitigation, this should not create additional requirements.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Tsk Force comprised of representatives of each committee. the Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs. | Ongoing | This review process has started. Several new compliance measures have been proposed. Approximately 50 of the measures proposed or field-tested during the first five (5) years of the NERC Compliance Pilot have been forwarded.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process. |  | N/A ERCOT
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | 2004-06-30 | ERCOT itself performs the Control Area and Reliability Coordinator functions and will be audited, sometime after the first half of 2004. A self-assessment has been completed as the first step. There has been a suggestion that Transmission Operators should also be audited; this is not established at this point. Many questions came up that are outside of ERCOT's direct responsibility, such as maintenance of lines and equipment and control settings of generators.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | The assessment documents and questionnaires related to initial audits of First Energy and MISO are the basis for this. Audits are on-going, the process again is based on existing NERC Certification procedures, which are similar to old ERCOT processes from the early 1990's.
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | NERC will likely help assemble a team for ERCOT audit as in 2001 and 2001. FERC or PUCT participation in ERCOT audits is not established.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | A draft NERC compliance measure has been proposed. Compliance requests that OWG review and add these requirements to the Operating Guides once the NERC measure is released.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | ERCOT needs to request that its transmission companies complete this for 2004, NERC is only requiring 345kV line reporting. Compliance requests that OWG discuss this to aid with consistent implementation.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | ERCOT transmission companies will need to assemble such documents. NERC standard will apply to 345kV owners; ERCOT may choose to broaden this. Again, Compliance requests that OWG discuss this to aid with consistent implementation.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | The ERCOT significant event investigation process developed last Fall includes provisions for Compliance to track recommendations resulting from events inside ERCOT. Followup on audits and observed non-compliance is handled through ERCOT Compliance processes, except for quarterly reporting to the NERC Board. Compliance will take the role of reporting on progress with the NERC Board's blackout recommendations.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance. |  | Not sure exactly what this means in ERCOT or elsewhere yet. Certain compliance measures assess operational performance and are assessed or reviewed monthly, these will likely be the basis for this function. It probably means more submittals to NERC throughout the year.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | This applies to ERCOT and its transmission operators,
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the Region | This may result in future requirements, but ERCOT's Planning Committee representative will have to keep the Region informed.
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC Board. |  | N/A ERCOT
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | ERCOT 345kV transmission owners should perform this review by Sept 30. The SPWG has discussed what ratings to use and what conditions to model, as well as how to interpret the term "extreme emergency". Compliance has asked SPWG members to confirm whether they can accomplish this by Sept. 30 and we will report at the next ROS meeting in April. The general outlook among SPWG members was that these settings are not likely to be a problem, but the detailed review needs to be completed before it is known whether any relays need adjustment.
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | ERCOT has under-voltage load shedding in the Rio Grande Valley. Compliance requests that ROS assign this task to the Regional planning groups or other stakeholder body to confirm whether the risk exists, and evaluate the costs. This work is to be completed by February 2005.
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement. | Ongoing | This may result in future requirements, but ERCOT's Planning Committee representative will have to keep the Region informed.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities. • Evaluate and improve the tools and procedures for operator and reliabililty coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators. | Ongoing | This may result in future requirements, but ERCOT's Operating Committee representative will have to keep the Region informed. Revisions of Policy 4,5,6 and 9 are underway.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices. | Ongoing | This may result in future requirements, but ERCOT's Operating Committee representative will have to keep the Region informed.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement. |  | N/A to ERCOT except for the Planning and Operating Committee representatives.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | ERCOT will need to review these after release, probably March 2005.
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | SPWG discussed this briefly at their February 2004 meeting; most relays with recording capability do not have time synchronization, but almost all dedicated fault recorders do. ERCOT will want to change the Operating Guides to define which locations need time synchronization. Discussions should also address generator recording devices and make clear where generators have responsibility. Compliance requests that ROS direct SPWG to develop the necessary changes for their next scheduled meeting.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Followup to 12a, may require ERCOT companies to install equipment to allow time synchronization. ERCOT should define a time schedule for compliance when the Operating Guides are reviewed. ERCOT has never defined dynamic data recorder requirements and will need to assign this task to DWG and SPWG or other groups.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year. |  | This may result in future requirements, but ERCOT's Operating Committee representative will have to keep the Region informed.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required. |  | N/A to ERCOT
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | This may result in future requirements, but ERCOT's Planning Committee representative will have to keep the Region informed. ROS may want to assign review of NERC recommendations or suggestions to SSWG and DWG.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | ERCOT will need to assign a group to define what will be done here for modeling data. ERCOT lacks specific requirements to compare models with actual system performance. Some activities such as Operation and Planning model cross-checking, fault current review and certain generator tests may meet part of this recommendation, but criteria are not established, and other areas should perhaps be considered. Inter-regional data exchange doesn't apply in ERCOT except regarding DC ties and planned transactions, and Swing-Between-Grid plants.

## COG (hidden)
ERCOT Compliance Group Tasks Related to NERC Board Recommendations on Blackout Status - Initial Draft April 6, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthermore, each organization shall present its detailed plan for completing these actions to the NERC committees for technical review on March 23-24, 2004, and to the NERC board for approval no later than April 2, 2004.
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity may seek technical assistance.
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | ERCOT Compliance currently reports on frequency control and transmission security violations on a monthly basis, or can without significant additional effort. Quarterly reports to the NERC Board started in 2003. Additional information may need to be added to this reporting, which does not presently address all NERC measures and addresses no ERCOT-specific standards.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | This suggests that NERC's Board will assist enforcement and mitigation of non-compliance. Details are lacking, but unless NERC makes demands beyond those determined by ERCOT in its compliance process for mitigation, this should not create additional requirements.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Tsk Force comprised of representatives of each committee. the Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs. | Ongoing | This review process has started. Several new compliance measures have been proposed. Approximately 50 of the measures proposed or field-tested during the first five (5) years of the NERC Compliance Pilot have been forwarded.
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | Ongoing | ERCOT itself performs the Control Area and Reliability Coordinator functions and will be audited, sometime after the first half of 2004. A self-assessment has been completed as the first step. There has been a suggestion that Transmission Operators should also be audited; this is not established at this point. Many questions came up that are outside of ERCOT's direct responsibility, such as maintenance of lines and equipment and control settings of generators.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | The assessment documents and questionnaires related to initial audits of First Energy and MISO are the basis for this. Audits are on-going, the process again is based on existing NERC Certification procedures, which are similar to old ERCOT processes from the early 1990's.
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | NERC will likely help assemble a team for ERCOT audit as in 2001 and 2001. FERC or PUCT participation in ERCOT audits is not established.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | Primary responsibility assigned to the SERC OC Task Force.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | Primary responsibility assigned to the SERC OC Task Force.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | Primary responsibility assigned to the SERC OC Task Force.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | A draft NERC compliance measure has been proposed. Compliance requests that OWG review and add these requirements to the Operating Guides once the NERC measure is released.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. |  | ERCOT needs to request that its transmission companies complete this for 2004, NERC is only requiring 345kV line reporting. Compliance requests that OWG discuss this to aid with consistent implementation.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | Primary responsibility assigned to the SERC staff and the SERC Compliance Oversight Group (COG). Secondary support from: - EC CRSC - OC CS - EC Task Force - OC Task Force Secondary support needed to ensure adequate information is provided from both operations and planning.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | Primary responsibility assigned to the SERC OC System Operator Subcommittee.
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the SERC Region | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Working Group
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | Primary responsibility assigned to the SERC EC Task Force with secondary support from the EC Protection and Control Subcommittee
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups and other group(s): - Reliability Review Subcommittee - Protection and Control Subcommittee - VST
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | Primary responsibility assigned to the SERC OC Operations Planning Subcommittee.
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | Primary responsibility assigned to the SERC Protection and Control Subcommittee with secondary support from the following: - VST Stability Study Group - EC Task Force - OC Task Force Status to date: The SERC EC PCS asked the VST Steering Committee in Dec. 2003 to perform a study to determine the desired (for regional reliability purposes) locations of DDR installations in the SERC Region. The VST Steering Committee assigned this study to the VST Stability Study Group (VSTSSG). The VSTSSG plans to send a preliminary list of desired locations to the PCS for review. The PCS will provide a list of all existing devices that are already installed at the desired locations and installations that are in close proximity for the VSTSSG to review. The VSTSSG will determine if the installations that are nearby the desired locations are adequate and will update the regional location list. Once the location list is finalized, the PCS will report this to the respective EC and OC Task Forces for implementation in the SERC Region.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the SERC EC Protection and Control Subcommittee.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | Primary responsibility assigned to the SERC EC Reliability Review Subcommittee with secondary support from the SERC EC Task Force.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the following: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Subcommittee - VST Note: the involvement of the SERC OC Task Force is necessary to incorporate actual system performance in the model validation process.

## EC CRSC (hidden)
SERC EC Compliance Review Steering Committee (CRSC) Tasks Related to NERC Board Recommendations on Blackout Status - Revised March 3, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthe
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC staff. Secondary support assigned to the following: - EC Compliance Review Steering Committee (CRSC) - OC Compliance Subcommittee (CS) No significant violations have been reported in the SERC Region to date.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC staff. Secondary support assigned to the following: - EC Compliance Review Steering Committee (CRSC) - OC Compliance Subcommittee (CS) No significant violations have been reported in the SERC Region to date.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | 2004-06-30 | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC staff. Secondary support assigned to the following: - EC Compliance Review Steering Committee (CRSC) - OC Compliance Subcommittee (CS)
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | Primary responsibility assigned to the SERC OC Task Force.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | Primary responsibility assigned to the SERC OC Task Force.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | Primary responsibility assigned to the SERC OC Task Force.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | Primary responsibility assigned to the SERC staff and the SERC Compliance Oversight Group (COG). Secondary support from: - EC CRSC - OC CS - EC Task Force - OC Task Force Secondary support needed to ensure adequate information is provided from both operations and planning.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | Primary responsibility assigned to the SERC OC System Operator Subcommittee.
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the SERC Region | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Working Group
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | Primary responsibility assigned to the SERC EC Task Force with secondary support from the EC Protection and Control Subcommittee
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups and other group(s): - Reliability Review Subcommittee - Protection and Control Subcommittee - VST
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | Primary responsibility assigned to the SERC OC Operations Planning Subcommittee.
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | Primary responsibility assigned to the SERC Protection and Control Subcommittee with secondary support from the following: - VST Stability Study Group - EC Task Force - OC Task Force Status to date: The SERC EC PCS asked the VST Steering Committee in Dec. 2003 to perform a study to determine the desired (for regional reliability purposes) locations of DDR installations in the SERC Region. The VST Steering Committee assigned this study to the VST Stability Study Group (VSTSSG). The VSTSSG plans to send a preliminary list of desired locations to the PCS for review. The PCS will provide a list of all existing devices that are already installed at the desired locations and installations that are in close proximity for the VSTSSG to review. The VSTSSG will determine if the installations that are nearby the desired locations are adequate and will update the regional location list. Once the location list is finalized, the PCS will report this to the respective EC and OC Task Forces for implementation in the SERC Region.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the SERC EC Protection and Control Subcommittee.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | Primary responsibility assigned to the SERC EC Reliability Review Subcommittee with secondary support from the SERC EC Task Force.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the following: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Subcommittee - VST Note: the involvement of the SERC OC Task Force is necessary to incorporate actual system performance in the model validation process.

## OC CS (hidden)
SERC OC Compliance Subcommittee (CS) Tasks Related to NERC Board Recommendations on Blackout Status - Revised March 3, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthe
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC staff. Secondary support assigned to the following: - EC Compliance Review Steering Committee (CRSC) - OC Compliance Subcommittee (CS) No significant violations have been reported in the SERC Region to date.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC staff. Secondary support assigned to the following: - EC Compliance Review Steering Committee (CRSC) - OC Compliance Subcommittee (CS) No significant violations have been reported in the SERC Region to date.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | 2004-06-30 | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC staff. Secondary support assigned to the following: - EC Compliance Review Steering Committee (CRSC) - OC Compliance Subcommittee (CS)
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | Primary responsibility assigned to the SERC OC Task Force.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | Primary responsibility assigned to the SERC OC Task Force.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | Primary responsibility assigned to the SERC OC Task Force.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | Primary responsibility assigned to the SERC staff and the SERC Compliance Oversight Group (COG). Secondary support from: - EC CRSC - OC CS - EC Task Force - OC Task Force Secondary support needed to ensure adequate information is provided from both operations and planning.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | Primary responsibility assigned to the SERC OC System Operator Subcommittee.
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the SERC Region | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Working Group
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | Primary responsibility assigned to the SERC EC Task Force with secondary support from the EC Protection and Control Subcommittee
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups and other group(s): - Reliability Review Subcommittee - Protection and Control Subcommittee - VST
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | Primary responsibility assigned to the SERC OC Operations Planning Subcommittee.
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | Primary responsibility assigned to the SERC Protection and Control Subcommittee with secondary support from the following: - VST Stability Study Group - EC Task Force - OC Task Force Status to date: The SERC EC PCS asked the VST Steering Committee in Dec. 2003 to perform a study to determine the desired (for regional reliability purposes) locations of DDR installations in the SERC Region. The VST Steering Committee assigned this study to the VST Stability Study Group (VSTSSG). The VSTSSG plans to send a preliminary list of desired locations to the PCS for review. The PCS will provide a list of all existing devices that are already installed at the desired locations and installations that are in close proximity for the VSTSSG to review. The VSTSSG will determine if the installations that are nearby the desired locations are adequate and will update the regional location list. Once the location list is finalized, the PCS will report this to the respective EC and OC Task Forces for implementation in the SERC Region.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the SERC EC Protection and Control Subcommittee.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | Primary responsibility assigned to the SERC EC Reliability Review Subcommittee with secondary support from the SERC EC Task Force.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the following: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Subcommittee - VST Note: the involvement of the SERC OC Task Force is necessary to incorporate actual system performance in the model validation process.

## EC TF (hidden)
SERC EC Task Force Tasks Related to NERC Board Recommendations on Blackout Status - Revised March 3, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthe
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | 2004-06-30 | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager.
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | Primary responsibility assigned to the SERC OC Task Force.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | Primary responsibility assigned to the SERC OC Task Force.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | Primary responsibility assigned to the SERC OC Task Force.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | Primary responsibility assigned to the SERC staff and the SERC Compliance Oversight Group (COG). Secondary support from: - EC CRSC - OC CS - EC Task Force - OC Task Force Secondary support needed to ensure adequate information is provided from both operations and planning.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | Primary responsibility assigned to the SERC OC System Operator Subcommittee.
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the SERC Region | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups: - Reliability Review Subcommittee (RRS) - Generation Subcommittee (GS) - Stability Database Working Group (SDWG)
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | Primary responsibility assigned to the SERC EC Task Force with secondary support from the EC Protection and Control Subcommittee (PCS).
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups and other group(s): - Reliability Review Subcommittee - Protection and Control Subcommittee - VST
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | Primary responsibility assigned to the SERC OC Operations Planning Subcommittee.
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | Primary responsibility assigned to the SERC Protection and Control Subcommittee (PCS) with secondary support from the following: - VST Stability Study Group (VSTSSG) - EC Task Force - OC Task Force Status to date: The SERC EC PCS asked the VST Steering Committee in Dec. 2003 to perform a study to determine the desired (for regional reliability purposes) locations of DDR installations in the SERC Region. The VST Steering Committee assigned this study to the VST Stability Study Group (VSTSSG). The VSTSSG plans to send a preliminary list of desired locations to the PCS for review. The PCS will provide a list of all existing devices that are already installed at the desired locations and installations that are in close proximity for the VSTSSG to review. The VSTSSG will determine if the installations that are nearby the desired locations are adequate and will update the regional location list. Once the location list is finalized, the PCS will report this to the respective EC and OC Task Forces for implementation in the SERC Region.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the SERC EC Protection and Control Subcommittee.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | Primary responsibility assigned to the SERC EC Reliability Review Subcommittee (RRS) with secondary support from the SERC EC Task Force.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the following: - Reliability Review Subcommittee (RRS) - Generation Subcommittee (GS) - Stability Database Working Group (SDWG) - VST Note: the involvement of the SERC OC Task Force is necessary to incorporate actual system performance in the model validation process.

## OC TF (hidden)
SERC OC Task Force Tasks Related to NERC Board Recommendations on Blackout Status - Revised March 3, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthe
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | 2004-06-30 | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager.
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | Assignments will be determined by the SERC EC and OC Executive Committees following input from the breakout session discussions at the March 2004 SERC Joint Meeting.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | Assignments will be determined by the SERC EC and OC Executive Committees following input from the breakout session discussions at the March 2004 SERC Joint Meeting.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | Assignments will be determined by the SERC EC and OC Executive Committees following input from the breakout session discussions at the March 2004 SERC Joint Meeting.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | Primary responsibility assigned to the SERC staff and the SERC Compliance Oversight Group (COG). Secondary support from: - EC CRSC - OC CS - EC Task Force - OC Task Force Secondary support needed to ensure adequate information is provided from both operations and planning.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | Primary responsibility assigned to the SERC OC System Operator Subcommittee.
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the SERC Region | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Working Group
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | Primary responsibility assigned to the SERC EC Task Force with secondary support from the EC Protection and Control Subcommittee
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups and other group(s): - Reliability Review Subcommittee - Protection and Control Subcommittee - VST
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | Primary responsibility assigned to the SERC OC Operations Planning Subcommittee.
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | Primary responsibility assigned to the SERC Protection and Control Subcommittee (PCS) with secondary support from the following: - VST Stability Study Group (VSTSSG) - EC Task Force - OC Task Force Status to date: The SERC EC PCS asked the VST Steering Committee in Dec. 2003 to perform a study to determine the desired (for regional reliability purposes) locations of DDR installations in the SERC Region. The VST Steering Committee assigned this study to the VST Stability Study Group (VSTSSG). The VSTSSG plans to send a preliminary list of desired locations to the PCS for review. The PCS will provide a list of all existing devices that are already installed at the desired locations and installations that are in close proximity for the VSTSSG to review. The VSTSSG will determine if the installations that are nearby the desired locations are adequate and will update the regional location list. Once the location list is finalized, the PCS will report this to the respective EC and OC Task Forces for implementation in the SERC Region.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the SERC EC Protection and Control Subcommittee.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | Primary responsibility assigned to the SERC EC Reliability Review Subcommittee with secondary support from the SERC EC Task Force.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the following: - Reliability Review Subcommittee (RRS) - Generation Subcommittee (GS) - Stability Database Working Group (SDWG) - VST Note: the involvement of the SERC OC Task Force is necessary to incorporate actual system performance in the model validation process.

## EC RRS (hidden)
SERC EC Reliability Review Subcommittee (RRS) Tasks Related to NERC Board Recommendations on Blackout Status - Revised March 3, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthe
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | 2004-06-30 | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager.
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | Primary responsibility assigned to the SERC OC Task Force.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | Primary responsibility assigned to the SERC OC Task Force.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | Primary responsibility assigned to the SERC OC Task Force.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. Secondary support from the SERC EC CRSC, OC CS, EC Task Force, and OC Task Force. Secondary support needed to ensure adequate information is provided from both operations and planning.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | Primary responsibility assigned to the SERC OC System Operator Subcommittee.
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the SERC Region | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups: - Reliability Review Subcommittee (RRS) - Generation Subcommittee (GS) - Stability Database Working Group (SDWG)
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | Primary responsibility assigned to the SERC EC Task Force with secondary support from the EC Protection and Control Subcommittee
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups and other group(s): - Reliability Review Subcommittee - Protection and Control Subcommittee - VST
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | Primary responsibility assigned to the SERC OC Operations Planning Subcommittee.
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | Primary responsibility assigned to the SERC Protection and Control Subcommittee with secondary support from the following: - VST Stability Study Group - EC Task Force - OC Task Force Status to date: The SERC EC PCS asked the VST Steering Committee in Dec. 2003 to perform a study to determine the desired (for regional reliability purposes) locations of DDR installations in the SERC Region. The VST Steering Committee assigned this study to the VST Stability Study Group (VSTSSG). The VSTSSG plans to send a preliminary list of desired locations to the PCS for review. The PCS will provide a list of all existing devices that are already installed at the desired locations and installations that are in close proximity for the VSTSSG to review. The VSTSSG will determine if the installations that are nearby the desired locations are adequate and will update the regional location list. Once the location list is finalized, the PCS will report this to the respective EC and OC Task Forces for implementation in the SERC Region.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the SERC EC Protection and Control Subcommittee.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | Primary responsibility assigned to the SERC EC Reliability Review Subcommittee (RRS) with secondary support from the SERC EC Task Force.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the following: - Reliability Review Subcommittee (RRS) - Generation Subcommittee (GS) - Stability Database Working Group (SDWG) - VST Note: the involvement of the SERC OC Task Force is necessary to incorporate actual system performance in the model validation process.

## EC PCS (hidden)
SERC EC Protection and Control Subcommittee (PCS) Tasks Related to NERC Board Recommendations on Blackout Status - Revised March 3, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthe
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | 2004-06-30 | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager.
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | Primary responsibility assigned to the SERC OC Task Force.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | Primary responsibility assigned to the SERC OC Task Force.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | Primary responsibility assigned to the SERC OC Task Force.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. Secondary support from the SERC EC CRSC, OC CS, EC Task Force, and OC Task Force. Secondary support needed to ensure adequate information is provided from both operations and planning.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | Primary responsibility assigned to the SERC OC System Operator Subcommittee.
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the SERC Region | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Working Group
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | Primary responsibility assigned to the SERC EC Task Force with secondary support from the EC Protection and Control Subcommittee (PCS).
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups and other group(s): - Reliability Review Subcommittee - Protection and Control Subcommittee - VST
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | Primary responsibility assigned to the SERC OC Operations Planning Subcommittee.
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | Primary responsibility assigned to the SERC Protection and Control Subcommittee (PCS) with secondary support from the following: - VST Stability Study Group (VSTSSG) - EC Task Force - OC Task Force Status to date: The SERC EC PCS asked the VST Steering Committee in Dec. 2003 to perform a study to determine the desired (for regional reliability purposes) locations of DDR installations in the SERC Region. The VST Steering Committee assigned this study to the VST Stability Study Group (VSTSSG). The VSTSSG plans to send a preliminary list of desired locations to the PCS for review. The PCS will provide a list of all existing devices that are already installed at the desired locations and installations that are in close proximity for the VSTSSG to review. The VSTSSG will determine if the installations that are nearby the desired locations are adequate and will update the regional location list. Once the location list is finalized, the PCS will report this to the respective EC and OC Task Forces for implementation in the SERC Region.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the SERC EC Protection and Control Subcommittee.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | Primary responsibility assigned to the SERC EC Reliability Review Subcommittee with secondary support from the SERC EC Task Force.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the following: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Subcommittee - VST Note: the involvement of the SERC OC Task Force is necessary to incorporate actual system performance in the model validation process.

## EC GS (hidden)
SERC EC Generation Subcommittee (GS) Tasks Related to NERC Board Recommendations on Blackout Status - Revised March 3, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthe
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | 2004-06-30 | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager.
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | Primary responsibility assigned to the SERC OC Task Force.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | Primary responsibility assigned to the SERC OC Task Force.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | Primary responsibility assigned to the SERC OC Task Force.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. Secondary support from the SERC EC CRSC, OC CS, EC Task Force, and OC Task Force. Secondary support needed to ensure adequate information is provided from both operations and planning.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | Primary responsibility assigned to the SERC OC System Operator Subcommittee.
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the SERC Region | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups: - Reliability Review Subcommittee (RRS) - Generation Subcommittee (GS) - Stability Database Working Group (SDWG)
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | Primary responsibility assigned to the SERC EC Task Force with secondary support from the EC Protection and Control Subcommittee
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups and other group(s): - Reliability Review Subcommittee - Protection and Control Subcommittee - VST
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | Primary responsibility assigned to the SERC OC Operations Planning Subcommittee.
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | Primary responsibility assigned to the SERC Protection and Control Subcommittee with secondary support from the following: - VST Stability Study Group - EC Task Force - OC Task Force Status to date: The SERC EC PCS asked the VST Steering Committee in Dec. 2003 to perform a study to determine the desired (for regional reliability purposes) locations of DDR installations in the SERC Region. The VST Steering Committee assigned this study to the VST Stability Study Group (VSTSSG). The VSTSSG plans to send a preliminary list of desired locations to the PCS for review. The PCS will provide a list of all existing devices that are already installed at the desired locations and installations that are in close proximity for the VSTSSG to review. The VSTSSG will determine if the installations that are nearby the desired locations are adequate and will update the regional location list. Once the location list is finalized, the PCS will report this to the respective EC and OC Task Forces for implementation in the SERC Region.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the SERC EC Protection and Control Subcommittee.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | Primary responsibility assigned to the SERC EC Reliability Review Subcommittee with secondary support from the SERC EC Task Force.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the following: - Reliability Review Subcommittee (RRS) - Generation Subcommittee (GS) - Stability Database Working Group (SDWG) - VST Note: the involvement of the SERC OC Task Force is necessary to incorporate actual system performance in the model validation process.

## EC SDWG (hidden)
SERC EC Stability Database Working Group (SDWG) Tasks Related to NERC Board Recommendations on Blackout Status - Revised March 3, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthe
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | 2004-06-30 | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager.
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | Primary responsibility assigned to the SERC OC Task Force.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | Primary responsibility assigned to the SERC OC Task Force.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | Primary responsibility assigned to the SERC OC Task Force.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. Secondary support from the SERC EC CRSC, OC CS, EC Task Force, and OC Task Force. Secondary support needed to ensure adequate information is provided from both operations and planning.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | Primary responsibility assigned to the SERC OC System Operator Subcommittee.
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the SERC Region | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups: - Reliability Review Subcommittee (RRS) - Generation Subcommittee (GS) - Stability Database Working Group (SDWG)
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | Primary responsibility assigned to the SERC EC Task Force with secondary support from the EC Protection and Control Subcommittee
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups and other group(s): - Reliability Review Subcommittee - Protection and Control Subcommittee - VST
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | Primary responsibility assigned to the SERC OC Operations Planning Subcommittee.
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | Primary responsibility assigned to the SERC Protection and Control Subcommittee with secondary support from the following: - VST Stability Study Group - EC Task Force - OC Task Force Status to date: The SERC EC PCS asked the VST Steering Committee in Dec. 2003 to perform a study to determine the desired (for regional reliability purposes) locations of DDR installations in the SERC Region. The VST Steering Committee assigned this study to the VST Stability Study Group (VSTSSG). The VSTSSG plans to send a preliminary list of desired locations to the PCS for review. The PCS will provide a list of all existing devices that are already installed at the desired locations and installations that are in close proximity for the VSTSSG to review. The VSTSSG will determine if the installations that are nearby the desired locations are adequate and will update the regional location list. Once the location list is finalized, the PCS will report this to the respective EC and OC Task Forces for implementation in the SERC Region.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the SERC EC Protection and Control Subcommittee.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | Primary responsibility assigned to the SERC EC Reliability Review Subcommittee with secondary support from the SERC EC Task Force.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the following: - Reliability Review Subcommittee (RRS) - Generation Subcommittee (GS) - Stability Database Working Group (SDWG) - VST Note: the involvement of the SERC OC Task Force is necessary to incorporate actual system performance in the model validation process.

## EC PSS (hidden)
SERC EC Planning Standards Subcommittee (PSS) Tasks Related to NERC Board Recommendations on Blackout Status - Revised March 3, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthe
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | 2004-06-30 | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager.
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | Primary responsibility assigned to the SERC OC Task Force.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | Primary responsibility assigned to the SERC OC Task Force.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | Primary responsibility assigned to the SERC OC Task Force.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. Secondary support from the SERC EC CRSC, OC CS, EC Task Force, and OC Task Force. Secondary support needed to ensure adequate information is provided from both operations and planning.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | Primary responsibility assigned to the SERC OC System Operator Subcommittee.
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the SERC Region | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Working Group
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | Primary responsibility assigned to the SERC EC Task Force with secondary support from the EC Protection and Control Subcommittee
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups and other group(s): - Reliability Review Subcommittee - Protection and Control Subcommittee - VST
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | Primary responsibility assigned to the SERC OC Operations Planning Subcommittee.
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | Primary responsibility assigned to the SERC Protection and Control Subcommittee with secondary support from the following: - VST Stability Study Group - EC Task Force - OC Task Force Status to date: The SERC EC PCS asked the VST Steering Committee in Dec. 2003 to perform a study to determine the desired (for regional reliability purposes) locations of DDR installations in the SERC Region. The VST Steering Committee assigned this study to the VST Stability Study Group (VSTSSG). The VSTSSG plans to send a preliminary list of desired locations to the PCS for review. The PCS will provide a list of all existing devices that are already installed at the desired locations and installations that are in close proximity for the VSTSSG to review. The VSTSSG will determine if the installations that are nearby the desired locations are adequate and will update the regional location list. Once the location list is finalized, the PCS will report this to the respective EC and OC Task Forces for implementation in the SERC Region.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the SERC EC Protection and Control Subcommittee.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | Primary responsibility assigned to the SERC EC Reliability Review Subcommittee with secondary support from the SERC EC Task Force.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the following: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Subcommittee - VST Note: the involvement of the SERC OC Task Force is necessary to incorporate actual system performance in the model validation process.

## VST (hidden)
VST Tasks Related to NERC Board Recommendations on Blackout Status - Revised March 3, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthe
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | 2004-06-30 | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager.
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | Primary responsibility assigned to the SERC OC Task Force.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | Primary responsibility assigned to the SERC OC Task Force.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | Primary responsibility assigned to the SERC OC Task Force.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. Secondary support from the SERC EC CRSC, OC CS, EC Task Force, and OC Task Force. Secondary support needed to ensure adequate information is provided from both operations and planning.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | Primary responsibility assigned to the SERC OC System Operator Subcommittee.
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the SERC Region | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Working Group
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | Primary responsibility assigned to the SERC EC Task Force with secondary support from the EC Protection and Control Subcommittee
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups and other group(s): - Reliability Review Subcommittee - Protection and Control Subcommittee - VST
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | Primary responsibility assigned to the SERC OC Operations Planning Subcommittee.
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | Primary responsibility assigned to the SERC Protection and Control Subcommittee (PCS) with secondary support from the following: - VST Stability Study Group (VSTSSG) - EC Task Force - OC Task Force Status to date: The SERC EC PCS asked the VST Steering Committee in Dec. 2003 to perform a study to determine the desired (for regional reliability purposes) locations of DDR installations in the SERC Region. The VST Steering Committee assigned this study to the VST Stability Study Group (VSTSSG). The VSTSSG plans to send a preliminary list of desired locations to the PCS for review. The PCS will provide a list of all existing devices that are already installed at the desired locations and installations that are in close proximity for the VSTSSG to review. The VSTSSG will determine if the installations that are nearby the desired locations are adequate and will update the regional location list. Once the location list is finalized, the PCS will report this to the respective EC and OC Task Forces for implementation in the SERC Region.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the SERC EC Protection and Control Subcommittee.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | Primary responsibility assigned to the SERC EC Reliability Review Subcommittee with secondary support from the SERC EC Task Force.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the following: - Reliability Review Subcommittee (RRS) - Generation Subcommittee (GS) - Stability Database Working Group (SDWG) - VST Note: the involvement of the SERC OC Task Force is necessary to incorporate actual system performance in the model validation process.

## OC OPS (hidden)
SERC OC Operations Planning Subcommittee (OPS) Tasks Related to NERC Board Recommendations on Blackout Status - Revised March 2, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthe
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | 2004-06-30 | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager.
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | Primary responsibility assigned to the SERC OC Task Force.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | Primary responsibility assigned to the SERC OC Task Force.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | Primary responsibility assigned to the SERC OC Task Force.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. Secondary support from the SERC EC CRSC, OC CS, EC Task Force, and OC Task Force. Secondary support needed to ensure adequate information is provided from both operations and planning.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | Primary responsibility assigned to the SERC OC System Operator Subcommittee.
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the SERC Region | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Working Group
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | Primary responsibility assigned to the SERC EC Task Force with secondary support from the EC Protection and Control Subcommittee
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups and other group(s): - Reliability Review Subcommittee - Protection and Control Subcommittee - VST
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | Primary responsibility assigned to the SERC OC Operations Planning Subcommittee (OPS).
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | Primary responsibility assigned to the SERC Protection and Control Subcommittee with secondary support from the following: - VST Stability Study Group - EC Task Force - OC Task Force Status to date: The SERC EC PCS asked the VST Steering Committee in Dec. 2003 to perform a study to determine the desired (for regional reliability purposes) locations of DDR installations in the SERC Region. The VST Steering Committee assigned this study to the VST Stability Study Group (VSTSSG). The VSTSSG plans to send a preliminary list of desired locations to the PCS for review. The PCS will provide a list of all existing devices that are already installed at the desired locations and installations that are in close proximity for the VSTSSG to review. The VSTSSG will determine if the installations that are nearby the desired locations are adequate and will update the regional location list. Once the location list is finalized, the PCS will report this to the respective EC and OC Task Forces for implementation in the SERC Region.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the SERC EC Protection and Control Subcommittee.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | Primary responsibility assigned to the SERC EC Reliability Review Subcommittee with secondary support from the SERC EC Task Force.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the following: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Subcommittee - VST Note: the involvement of the SERC OC Task Force is necessary to incorporate actual system performance in the model validation process.

## OC SCS (hidden)
SERC OC Security Coordinator Subcommittee (SCS) Tasks Related to NERC Board Recommendations on Blackout Status - Revised March 2, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthe
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | 2004-06-30 | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager.
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | Primary responsibility assigned to the SERC OC Task Force.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | Primary responsibility assigned to the SERC OC Task Force.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | Primary responsibility assigned to the SERC OC Task Force.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. Secondary support from the SERC EC CRSC, OC CS, EC Task Force, and OC Task Force. Secondary support needed to ensure adequate information is provided from both operations and planning.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | Primary responsibility assigned to the SERC OC System Operator Subcommittee.
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the SERC Region | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Working Group
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | Primary responsibility assigned to the SERC EC Task Force with secondary support from the EC Protection and Control Subcommittee
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups and other group(s): - Reliability Review Subcommittee - Protection and Control Subcommittee - VST
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | Primary responsibility assigned to the SERC OC Operations Planning Subcommittee.
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | Primary responsibility assigned to the SERC Protection and Control Subcommittee with secondary support from the following: - VST Stability Study Group - EC Task Force - OC Task Force Status to date: The SERC EC PCS asked the VST Steering Committee in Dec. 2003 to perform a study to determine the desired (for regional reliability purposes) locations of DDR installations in the SERC Region. The VST Steering Committee assigned this study to the VST Stability Study Group (VSTSSG). The VSTSSG plans to send a preliminary list of desired locations to the PCS for review. The PCS will provide a list of all existing devices that are already installed at the desired locations and installations that are in close proximity for the VSTSSG to review. The VSTSSG will determine if the installations that are nearby the desired locations are adequate and will update the regional location list. Once the location list is finalized, the PCS will report this to the respective EC and OC Task Forces for implementation in the SERC Region.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the SERC EC Protection and Control Subcommittee.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | Primary responsibility assigned to the SERC EC Reliability Review Subcommittee with secondary support from the SERC EC Task Force.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the following: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Subcommittee - VST Note: the involvement of the SERC OC Task Force is necessary to incorporate actual system performance in the model validation process.

## OC SOS (hidden)
SERC OC System Operator Subcommittee (SOS) Tasks Related to NERC Board Recommendations on Blackout Status - Revised March 2, 2004
Rec. # | Recommendation | Milestone | Details and Status
1.a | Recommendation 1a: FE, MISO, and PJM shall each complete the remedial actions designated in Attachment A for their respective organizations and certify to the NERC board no later than June 30, 2004, that these specified actions have been completed. Furthe
1.b | Recommendation 1b: The NERC Technical Steering Committee shall immediately assign a team of experts to assist FE, MISO, and PJM in developing plans that adequately address the issues listed in Attachment A, and other remedial actions for which each entity
2.a | Recommendation 2a: Each regional reliability council shall report to the NERC Compliance Enforcement Program within one month of occurrence all significant violations of NERC operating policies and planning standards and regional standards, whether verified or still under investigation. Such reports shall confidentially note details regarding the nature and potential reliability impacts of the alleged violations and the identity of parties involved. Additionally, each regional reliability council shall report quarterly to NERC, in a format prescribed by NERC, all violations of NERC and regional reliability council standards. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.b | Recommendation 2b: Being presented with the results of the investigation of any significant violation, and with due consideration of the surrounding facts and circumstances, the NERC board shall require an offending organization to correct the violation within a specified time. If the board determines that an offending organization is non-responsive and continues to cause a risk to the reliability of the interconnected power systems, the board will seek to remedy the violation by requesting assistance of the appropriate regulatory authorities in the United States, Canada, and Mexico. | Ongoing | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. No significant violations have been reported in the SERC Region to date.
2.c | Recommendation 2c: The Planning and Operating Committees, working in conjunction with the Compliance Enforcement Program, shall review and update existing approved and draft compliance templates applicable to current NERC operating policies and planning standards; and submit any revisions or new templates to the board for approval no later than March 31, 2004. To expedite this task, the NERC President shall immediately form a Compliance Template Task Force comprised of representatives of each committee. The Compliance Enforcement Program shall issue the board-approved compliance templates to the regional reliability councils for adoption into their compliance monitoring programs.
2.d | Recommendation 2d: The NERC Compliance Enforcement Program and ECAR shall, within three months of the issuance of the final report from the Compliance and Standards investigation team, evaluate the identified violations of NERC and regional standards, as compared to previous compliance reviews and audits for the applicable entities, and develop recommendations to improve the compliance process.
3.a | Recommendation 3a: The NERC Compliance Enforcement Program and the regional reliability councils shall jointly establish a program to audit the reliability readiness of all reliability coordinators and control areas, with immediate attention given to addressing the deficiencies identified in the August 14 blackout investigation. Audits of all control areas and reliability coordinators shall be completed within three years and continue in a three-year cycle. The 20 highest priority audits, as determined by the Compliance Enforcement Program, will be completed by June 30, 2004. | 2004-06-30 | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
3.b | Recommendation 3b: NERC will establish a set of baseline audit criteria to which regional criteria may be added. The control area requirements will be based on the existing NERC Control Area Certification Procedure. Reliability coordinator audits will include evaluation of reliability plans, procedures, processes, tools, personnel qualifications, and training. In addition to reviewing written documents, the audits will carefully examine the actual practices and preparedness of control areas and reliability coordinators. |  | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager.
3.c | Recommendation 3c: The reliability regions, with the oversight and direct participation of NERC, will audit each control area’s and reliability coordinator’s readiness to meet these audit criteria. FERC and other relevant regulatory agencies will be invited to participate in the audits, subject to the same confidentiality conditions as the other members of the audit teams. |  | Representatives from the SERC OC Compliance Subcommittee and the EC Compliance Review Steering Committee as well as SERC staff including (SERC Compliance Manager and the OC Staff Engineer) have volunteered to participate on the NERC Readiness Audit Teams. All SERC Control Areas completed a readiness questionnaire by February 27, 2004.
4.a | Recommendation 4a: NERC and the regional reliability councils shall jointly initiate a program to report all bulk electric system transmission line trips resulting from vegetation contact. The program will use the successful WECC vegetation monitoring program as a model. |  | Primary responsibility assigned to the SERC OC Task Force.
4.b | Recommendation 4b: Beginning with an effective date of January 1, 2004, each transmission operator will submit an annual report of all vegetation-related high voltage line trips to its respective reliability region. Each region shall assemble a detailed annual report of vegetation related line trips in the region to NERC no later than March 31 for the preceding year, with the first reporting to be completed by March 2005 for calendar year 2004. | 2005-03-31 | Assignments will be determined by the SERC EC and OC Executive Committees following input from the breakout session discussions at the March 2004 SERC Joint Meeting.
4.c | Recommendation 4c: Each bulk electric transmission owner shall make its vegetation management procedure, and documentation of work completed, available for review and verification upon request by the applicable regional reliability council, NERC, or applicable federal, state or provincial regulatory agency. |  | Assignments will be determined by the SERC EC and OC Executive Committees following input from the breakout session discussions at the March 2004 SERC Joint Meeting.
5.a | Recommendation 5a: NERC and each regional reliability council shall establish a program for documenting completion of recommendations resulting from the August 14 blackout and other historical outages, as well as NERC and regional reports on violations of reliability standards, results of compliance audits, and lessons learned from system disturbances. Regions shall report quarterly to NERC on the status of follow-up actions to address recommendations, lessons learned, and areas noted for improvement. NERC staff shall report both NERC activities and a summary of regional activities to the board. | Respective NERC BOT Meeting Dates | Primary responsibility assigned to the SERC Compliance Oversight Group (COG) and the SERC Compliance Manager. Secondary support from the SERC EC CRSC, OC CS, EC Task Force, and OC Task Force. Secondary support needed to ensure adequate information is provided from both operations and planning.
5.b | Recommendation 5b: NERC shall by January 1, 2005 establish a reliability performance monitoring function to evaluate and report bulk electric system reliability performance.
6 | Recommendation 6: All reliability coordinators, control areas, and transmission operators shall provide at least five days per year of training and drills in system emergencies, using realistic simulations, for each staff person with responsibility for the real-time operation or reliability monitoring of the bulk electric system. This system emergency training is in addition to other training requirements. Five days of system emergency training and drills are to be completed prior to June 30, 2004, with credit given for documented training already completed since July 1, 2003. Training documents, including curriculum, training methods, and individual training records, are to be available for verification during reliability readiness audits. | June 30, 2004 and ongoing on a yearly basis | Primary responsibility assigned to the SERC OC System Operator Subcommittee (SOS).
7.a | Recommendation 7a: The Planning Committee shall reevaluate within one year the effectiveness of the existing reactive power and voltage control standards and how they are being implemented in practice in the ten NERC regions. Based on this evaluation, the Planning Committee shall recommend revisions to standards or process improvements to ensure voltage control and stability issues are adequately addressed. | due dates will be provided by the NERC PC to ask each region how reactive power and voltage control standards are being implemented in practice in the SERC Region | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Working Group
7.b | Recommendation 7b: ECAR shall no later than June 30, 2004 review its reactive power and voltage criteria and procedures, verify that its criteria and procedures are being fully implemented in regional and member studies and operations, and report the results to the NERC board.
8.a | Recommendation 8a: All transmission owners shall, no later than September 30, 2004, evaluate the zone 3 relay settings on all transmission lines operating at 230 kV and above for the purpose of verifying that each zone 3 relay is not set to trip on load under extreme emergency conditions6. In each case that a zone 3 relay is set so as to trip on load under extreme conditions, the transmission operator shall reset, upgrade, replace, or otherwise mitigate the overreach of those relays as soon as possible and on a priority basis, but no later than December 31, 2005. Upon completing analysis of its application of zone 3 relays, each transmission owner may no later than December 31, 2004 submit justification to NERC for applying zone 3 relays outside of these recommended parameters. The Planning Committee shall review such exceptions to ensure they do not increase the risk of widening a cascading failure of the power system. | September 30, 2004 December 31, 2004 December 31, 2005, respectively | Primary responsibility assigned to the SERC EC Task Force with secondary support from the EC Protection and Control Subcommittee
8.b | Recommendation 8b: Each regional reliability council shall complete an evaluation of the feasibility and benefits of installing under-voltage load shedding capability in load centers within the region that could become unstable as a result of being deficient in reactive power following credible multiple-contingency events. The regions are to complete the initial studies and report the results to NERC within one year. The regions are requested to promote the installation of under-voltage load shedding capabilities within critical areas, as determined by the studies to be effective in preventing an uncontrolled cascade of the power system. | 2005-02-10 | Primary responsibility assigned to the SERC EC Task Force with secondary support from the following EC subcommittees/working groups and other group(s): - Reliability Review Subcommittee - Protection and Control Subcommittee - VST
8.c | Recommendation 8c: The Planning Committee shall evaluate Planning Standard III – System Protection and Control and propose within one year specific revisions to the criteria to adequately address the issue of slowing or limiting the propagation of a cascading failure. The board directs the Planning Committee to evaluate the lessons from August 14 regarding relay protection design and application and offer additional recommendations for improvement.
9 | Recommendation 9: The Operating Committee shall complete the following by June 30, 2004: • Evaluate and revise the operating policies and procedures, or provide interpretations, to ensure reliability coordinator and control area functions, responsibilities, and authorities are completely and unambiguously defined. • Evaluate and improve the tools and procedures for operator and reliability coordinator communications during emergencies. • Evaluate and improve the tools and procedures for the timely exchange of outage information among control areas and reliability coordinators.
10 | Recommendation 10: The Operating Committee shall within one year evaluate the real-time operating tools necessary for reliable operation and reliability coordination, including backup capabilities. The Operating Committee is directed to report both minimum acceptable capabilities for critical reliability functions and a guide of best practices.
11.a | Recommendation 11a: The Planning Committee, working in conjunction with the Operating Committee, NPCC, ECAR, and PJM, shall evaluate the black start and system restoration performance following the outage of August 14, and within one year report to the NERC board the results of that evaluation with recommendations for improvement.
11.b | Recommendation 11b: All regional reliability councils shall, within six months of the Planning Committee report to the NERC board, reevaluate their procedures and plans to assure an effective blackstart and restoration capability within their region. | 2005-08-10 | Primary responsibility assigned to the SERC OC Operations Planning Subcommittee.
12.a | Recommendation 12a: The reliability regions, coordinated through the NERC Planning Committee, shall within one year define regional criteria for the application of synchronized recording devices in power plants and substations. Regions are requested to facilitate the installation of an appropriate number, type and location of devices within the region as soon as practical to allow accurate recording of future system disturbances and to facilitate benchmarking of simulation studies by comparison to actual disturbances. | 2005-02-10 | Primary responsibility assigned to the SERC Protection and Control Subcommittee with secondary support from the following: - VST Stability Study Group - EC Task Force - OC Task Force Status to date: The SERC EC PCS asked the VST Steering Committee in Dec. 2003 to perform a study to determine the desired (for regional reliability purposes) locations of DDR installations in the SERC Region. The VST Steering Committee assigned this study to the VST Stability Study Group (VSTSSG). The VSTSSG plans to send a preliminary list of desired locations to the PCS for review. The PCS will provide a list of all existing devices that are already installed at the desired locations and installations that are in close proximity for the VSTSSG to review. The VSTSSG will determine if the installations that are nearby the desired locations are adequate and will update the regional location list. Once the location list is finalized, the PCS will report this to the respective EC and OC Task Forces for implementation in the SERC Region.
12.b | Recommendation 12b: Facilities owners shall, in accordance with regional criteria, upgrade existing dynamic recorders to include GPS time synchronization and, as necessary, install additional dynamic recorders. | following implementation of 12a | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the SERC EC Protection and Control Subcommittee.
13.a | Recommendation 13a: The Operating Committee shall evaluate operations planning and operating criteria and recommend revisions in a report to the board within one year.
13.b | Recommendation 13b: ECAR shall no later than June 30, 2004 reevaluate its planning and study procedures and practices to ensure they are in compliance with NERC standards, ECAR Document No. 1, and other relevant criteria; and that ECAR and its members’ studies are being implemented as required.
13.c | Recommendation 13c: The Planning Committee, working in conjunction with the regional reliability councils, shall within two years reevaluate the criteria, methods and practices used for system design, planning and analysis; and shall report the results and recommendations to the NERC board. This review shall include an evaluation of transmission facility ratings methods and practices, and the sharing of consistent ratings information. | February 10, 2006 with interim milestones assigned by the NERC PC | Primary responsibility assigned to the SERC EC Reliability Review Subcommittee with secondary support from the SERC EC Task Force.
14 | Recommendation 14: The regional reliability councils shall within one year establish and begin implementing criteria and procedures for validating data used in power flow models and dynamic simulations by benchmarking model data with actual system performance. Validated modeling data shall be exchanged on an inter-regional basis as needed for reliable system planning and operation. | February 10, 2005 and ongoing | Primary Responsibility assigned jointly to the SERC EC and OC Task Forces with secondary support from the following: - Reliability Review Subcommittee - Generation Subcommittee - Stability Database Subcommittee - VST Note: the involvement of the SERC OC Task Force is necessary to incorporate actual system performance in the model validation process.

## Approved Recommendations
NERC Board Approved Blackout Recommendations