## NERC CPS Survey
CPS Form 1
Region: | ERCOT |  | Control Area: |  | ERCOT
L10 - | 131.0529 |  | Month - | 2004-07-31 | Year - | 2004-01-01 | e - | 30 mHz
| CPS1 |  |  |  | CPS2
Hour
Ending
CENTRAL |  |  | Number of |  |  |  | Unavailable
Time | CF | % | Samples |  | Violations |  | Periods
0100 | 751.98 | 116.4467 | 1860 |  | 35 |  | 0 |  | 9.6998 | 12.005
0200 | 526.06 | 141.5489 | 1824 |  | 13 |  | 4 |  | 2.0669 | 68.485
0300 | 699.98 | 122.2244 | 1860 |  | 22 |  | 0 |  | 4.888 | 25.005
0400 | 452.77 | 149.6922 | 1860 |  | 7 |  | 0 |  | 1.7244 | 86.8075
0500 | 356.39 | 160.4011 | 1860 |  | 6 |  | 0 |  | 1.4463 | 110.9025
0600 | 521.75 | 142.0278 | 1860 |  | 21 |  | 0 |  | 2.0417 | 69.5625
0700 | 693.33 | 122.9633 | 1860 |  | 39 |  | 0 |  | 4.611 | 26.6675
0800 | 468.58 | 147.9356 | 1860 |  | 15 |  | 0 |  | 1.7855 | 82.855
0900 | 672.75 | 125.25 | 1860 |  | 29 |  | 0 |  | 3.9371 | 31.8125
1000 | 666.95 | 125.8944 | 1813 |  | 25 |  | 4 |  | 3.7849 | 33.2625
1100 | 722.8 | 119.6889 | 1860 |  | 31 |  | 0 |  | 6.2015 | 19.3
1200 | 587.91 | 134.6767 | 1860 |  | 20 |  | 0 |  | 2.54 | 53.0225
1300 | 503.53 | 144.0522 | 1860 |  | 18 |  | 0 |  | 1.9436 | 74.1175
1400 | 395.2 | 156.0889 | 1859 |  | 10 |  | 0 |  | 1.5424 | 101.2
1500 | 317.85 | 164.6833 | 1857 |  | 10 |  | 0 |  | 1.3662 | 120.5375
1600 | 324.15 | 163.9833 | 1859 |  | 7 |  | 0 |  | 1.3784 | 118.9625
1700 | 300.34 | 166.6289 | 1853 |  | 3 |  | 0 |  | 1.3339 | 124.915
1800 | 259.45 | 171.1722 | 1858 |  | 2 |  | 1 |  | 1.2667 | 135.1375
1900 | 355.58 | 160.4911 | 1860 |  | 11 |  | 0 |  | 1.4445 | 111.105
2000 | 367.99 | 159.1122 | 1860 |  | 14 |  | 0 |  | 1.4732 | 108.0025
2100 | 382.88 | 157.4578 | 1860 |  | 20 |  | 0 |  | 1.51 | 104.28
2200 | 477.87 | 146.9033 | 1860 |  | 17 |  | 0 |  | 1.8241 | 80.5325
2300 | 665.77 | 126.0256 | 1860 |  | 26 |  | 0 |  | 3.7555 | 33.5575
2400 | 702.19 | 121.9789 | 1860 |  | 24 | Total =425 | 0 |  | 4.9884 | 24.4525
200
CPS1(%) |  |  |  | CPS2(%) | 425
Month | 507.2521 | 143.6387 | 44543 | Month | 90.4602 |  | 9
CF12-month
CPS1(%)
Notes:
Record the total number of samples for each of the 24 hour-averages
Record the total number of CPS2 violations for each of the 24 hour-periods during the month
Record the total number of unavailable ten-minute periods during the month for each of the 24 hour-periods
Record the total number of samples for each of the 24 hour-averages
Record the total number of CPS2 violations for each of the 24 hour-periods during the month
Record the total number of unavailable ten-minute periods during the month for each of the 24 hour-periods
Record the total number of samples for each of the 24 hour-averages
Record the total number of CPS2 violations for each of the 24 hour-periods during the month
Record the total number of unavailable ten-minute periods during the month for each of the 24 hour-periods
Record the total number of samples for each of the 24 hour-averages
Record the total number of CPS2 violations for each of the 24 hour-periods during the month
Record the total number of unavailable ten-minute periods during the month for each of the 24 hour-periods
Record the total number of samples for each of the 24 hour-averages
Record the total number of CPS2 violations for each of the 24 hour-periods during the month
Record the total number of unavailable ten-minute periods during the month for each of the 24 hour-periods
Record the total number of samples for each of the 24 hour-averages
Record the total number of CPS2 violations for each of the 24 hour-periods during the month
Record the total number of unavailable ten-minute periods during the month for each of the 24 hour-periods
Record the total number of samples for each of the 24 hour-averages
Record the total number of CPS2 violations for each of the 24 hour-periods during the month
Record the total number of unavailable ten-minute periods during the month for each of the 24 hour-periods

## Current Month
NERC Control Performance Standard Survey
Regional Summary
CPS Form 2
Region: ERCOT | Month: July | Year: 2004 | Date:7/01/04
Control Area |  | Control Performance Compliance
CPS1
Compliance
%
ERCOT |  | 143.64
* Calculated with an E1 of 30 MHz
CPS-July04.xls

## CPS 12 Month Rolling Average
CPS1 Twelve Month Rolling Average Through July 2004
12 Month
Rolling
Region: ERCOT | Average | 2004-01-01 | 2004-02-01 | 2004-03-01 | 2004-04-01 | 2004-05-01 | 2004-06-01 | 2004-07-01 | 2003-08-01 | 2003-09-01 | 2003-10-01 | 2003-11-01 | 2003-12-01
ERCOT | 127.5158 | 133.6 | 137 | 122.3 | 115.9 | 110.75 | 123.6 | 143.64 | 123 | 115.9 | 125.1 | 138.8 | 140.6
Notes: 1) CPS1 Standard requires rolling 12 month average performance of at least 100%
2) Calculated with an E1 of 30 MHz
CPS-July04.xls

## Graph Data
Month | CPS1 | 12 Month Rolling Average | Days | DayXMo Avg | Old Formula | Old Value | New Value | Normalized | Year | Cum Days | Cum Score | YTD Score
2001-08-01 | 127.3449 |  | 31 | 3947.6918 | 127.3449 | 290.6204 | 167.7088 | 127.3449 | 2001 | 153 | 12111.1737 | 79.158
2001-09-01 | 79.5371 |  | 30 | 2386.1125 | 79.5371 | 481.8517 | 146.4609 |  | 2002 | 365 | 38249.06 | 104.7919
2001-10-01 | 87.9611 |  | 31 | 2726.7955 | 87.9611 | 448.1554 | 150.205 |  | 2003 | 365 | 46198.605 | 126.5715
2001-11-01 | 62.178 |  | 30 | 1865.3406 | 62.178 | 551.2879 | 138.7458 |  | 2004 | 213 | 26976.99 | 126.6525
2001-12-01 | 38.2333 |  | 31 | 1185.2333 | 38.2333 | 647.0667 | 128.1037
2002-01-01 | 62.484 |  | 31 | 1937.0027 | 62.484 | 550.0642 | 138.8818
2002-02-01 | 68.4 |  | 28 | 1915.2 | 68.4 | 526.4 | 141.5111
2002-03-01 | 62.3779 |  | 31 | 1933.7154 | 62.3779 | 550.4883 | 138.8346 | e = 20
2002-04-01 | 64.6172 |  | 30 | 1938.5156 | 64.6172 | 541.5312 | 139.8299
2002-05-01 | 67.8633 |  | 31 | 2103.7612 | 67.8633 | 528.5469 | 141.2726
2002-06-01 | 83.0976 |  | 30 | 2492.9281 | 83.0976 | 467.6096 | 148.0434
2002-07-01 | 146.912 | 79.2505 | 31 | 4554.2731 |  |  | 146.912 | 143.8758 |  | -100 | 1200 | 66.6667
2002-08-01 | 152.6943 | 81.363 | 31 | 4733.522 |  |  | 152.6943 | 142.6246
2002-09-01 | 143.1144 | 86.6611 | 30 | 4293.4333 |  |  | 143.1144 | 142.3457
2002-10-01 | 129.6071 | 90.1316 | 31 | 4017.8196 |  |  | 129.6071 | 140.6292
2002-11-01 | 138.556 | 96.4964 | 30 | 4156.6792 |  |  | 138.556 | 140.6134
2002-12-01 | 134.5874 | 104.5259 | 31 | 4172.2096 |  |  | 134.5874 | 141.1537
2003-01-01 | 136.3305 | 110.6798 | 31 | 4226.2458 |  |  | 136.3305 | 140.9411
2003-02-01 | 121.7457 | 115.1253 | 28 | 3408.8794 |  |  | 121.7457 | 139.294
2003-03-01 | 129.2256 | 120.6959 | 31 | 4005.9922 |  |  | 129.2256 | 138.4932 | e = 30
2003-04-01 | 123.806 | 125.6283 | 30 | 3714.1792 |  |  | 123.806 | 137.1579
2003-05-01 | 110.6834 | 129.1967 | 31 | 3431.1862 |  |  | 110.6834 | 134.6088
2003-06-01 | 115.7107 | 131.9144 | 30 | 3471.3222 |  |  | 115.7107 | 131.9144
2003-07-01 | 137.1 | 131.0968 | 31 | 4250.1 |  |  | 137.1 | 131.0968
2003-08-01 | 123 | 128.6222 | 31 | 3813 |  |  | 123 | 128.6222
2003-09-01 | 115.9 | 126.3544 | 30 | 3477 |  |  | 115.9 | 126.3544
2003-10-01 | 125.1 | 125.9788 | 31 | 3878.1 |  |  | 125.1 | 125.9788
2003-11-01 | 138.8 | 125.9991 | 30 | 4164 |  |  | 138.8 | 125.9991
2003-12-02 | 140.6 | 126.5002 | 31 | 4358.6 |  |  | 140.6 | 126.5002
2004-01-01 | 133.6 | 126.2726 | 31 | 4141.6 |  |  | 133.6 | 126.2726
2004-02-01 | 137 | 127.5438 | 29 | 3973 |  |  | 137 | 127.5438
2004-03-01 | 122.3 | 126.9667 | 31 | 3791.3 |  |  | 122.3 | 126.9667
2004-04-01 | 115.9 | 126.3078 | 30 | 3477 |  |  | 115.9 | 126.3078
2004-05-01 | 110.75 | 126.3134 | 31 | 3433.25 |  |  | 110.75 | 126.3134
2004-06-01 | 123.6 | 126.9708 | 30 | 3708 |  |  | 123.6 | 126.9708
2004-07-01 | 143.64 | 127.5158 | 31 | 4452.84 |  |  | 143.64 | 127.5158
2004-08-01
2004-09-01
2004-10-01
2004-11-01
2004-12-02