## ERCOT Operations Report

## ROS & OWG

## May 2004

Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 5/3/2004 5:52 | 60.107 | 23564 | -641 | 809 | 4875 (1115) |
| 5/5/2004 6:06 | 59.898 | 25726 | 68 | -846 | 4845 (1050) |
| 5/6/2004 5:58 | 60.107 | 25825 | -2 | 466 | 5185 (1090) |
| 5/8/2004 15:03 | 60.107 | 33927 | 235 | 305 | N/A |
| 5/10/2004 11:28 | 60.107 | 35496 | 242 | -92 | Steel mill activity observed. |
| 5/11/2004 11:21 | 60.106 | 35665 | 163 | -183 | Steel mill activity observed. |
| 5/13/2004 22:00 | 59.890 | 31045 | -288 | -962 | -5060 (-1075) |
| 5/16/2004 6:04 | 60.171 | 22251 | -769 | 1311 | 645 (880) |
| 5/17/2004 6:03 | 60.130 | 27745 | -854 | 559 | 4590 (950) |
| 5/18/2004 6:00 | 60.111 | 29346 | -944 | 780 | 4100 (1075) |
| 5/19/2004 13:34 | 60.129 | 43235 | 73 | 63 | Frequency low 13:15 - 13:25 Maximum Up Regulation Deployed over the 10 minute period. |
| 5/21/2004 7:33 | 60.102 | 32719 | -299 | 350 | N/A |
| 5/26/2004 13:17 | 59.866 | 43600 | 850 | -778 | Bad STLF generated. |
| 5/26/2004 16:10 | 59.865 | 47068 | 850 | -1739 | 300 MW (2 units) runback at 16:00. Max Up Reg 16:07 - 16:30. At 17:00 Deployed to Maximum Down Reg. |
| 5/26/2004 16:52 | 60.110 | 47294 | -612 | -627 |  |
| 5/29/2004 1:07 | 60.101 | 31005 | -560 | 321 | -1000 (-250) |
| 5/31/2004 6:00 | 60.105 | 28839 | -746 | 793 | 1375 (775) |

Disturbances

| Time | Freq | MW LOST |
| --- | --- | --- |
| 5/11/2004 15:30 | 59.896 | 157 |
| 5/13/2004 3:03 | 59.879 | 350 |
| 5/15/2004 9:06 | 59.848 | 620 Runback over ~7 minutes |
| 5/15/2004 9:32 | 60.122 |  |
| 5/18/2004 20:43 | 59.825 | 650 |
| 5/19/2004 17:30 | 59.816 | 650 |
| 5/20/2004 14:41 | 59.871 | 565 |
| 5/28/2004 2:07 | 59.877 | 380 |
| 5/31/2004 15:33 | 59.899 | 360 |

Deployed Responsive (Reported Above)

| 5/1/04 3:21:22 | 5/11/04 6:03:40 | 5/15/04 11:13:48 | 5/26/04 6:04:26 |
| --- | --- | --- | --- |
| 5/1/04 4:47:44 | 5/11/04 7:58:54 | 5/16/04 23:02:18 | 5/26/04 13:12:56 |
| 5/2/04 6:06:58 | 5/11/04 10:59:08 | 5/18/04 20:38:40 | 5/26/04 16:06:16 |
| 5/5/04 5:35:02 | 5/11/04 15:30:14 | 5/19/04 6:09:52 | 5/26/04 23:16:36 |
| 5/5/04 6:06:24 | 5/11/04 21:59:20 | 5/19/04 12:05:12 | 5/27/04 5:01:04 |
| 5/5/04 22:08:08 | 5/11/04 23:18:38 | 5/19/04 17:30:40 | 5/27/04 12:03:54 |
| 5/6/04 6:06:24 | 5/12/04 14:24:58 | 5/20/04 7:21:20 | 5/28/04 2:07:52 |
| 5/6/04 12:59:36 | 5/12/04 15:50:42 | 5/20/04 14:41:20 | 5/29/04 2:31:12 |
| 5/6/04 23:16:46 | 5/13/04 3:02:37 | 5/22/04 6:05:50 | 5/30/04 0:03:28 |
| 5/7/04 11:03:50 | 5/13/04 6:05:08 | 5/22/04 14:25:32 | 5/30/04 21:59:30 |
| 5/8/04 14:59:16 | 5/13/04 21:57:54 | 5/23/04 6:05:20 | 5/31/04 8:17:28 |
| 5/11/04 0:48:34 | 5/15/04 9:03:08 | 5/23/04 23:33:40 | 5/31/04 15:33:36 |

# Locations and Relative Activity of Congestion Management

| Historical | May '03 | April '04 | May '04 |
| --- | --- | --- | --- |
| DFW | 179 | 77 | 133 |
| E RIO | 159 | 48 | 68 |
| W RIO | 71 | 6 | 31 |
| Laredo | 74 | 47 | 57 |
| Rio Pecos | 31 | 0 | 0 |
| Corpus | 31 | 27 | 31 |
| Abilene | 26 | 41 | 24 |
| San Angelo | 26 | 30 | 28 |
| Western | 8 | 6 | 17 |
| Houston | 49 | 1 | 0 |
| San Antonio | 31 | 19 | 0 |
|  | 701 | 302 | 389 |

| Contingency | Overload | Occurrences |
| --- | --- | --- |
| Lon Hill - Whitepoint | Nueces Bay - Whitepoint | 21 |
| N McCallen - N Edinburg | Polk - Hall Acres | 18 |
| Allen Switch - Royse Switch/Monticello | Allen Switch - Ben Davis | 14 |
| Midland East - Odessa | Odessa - Big Three | 10 |
| South - Houston CSC |  | 9 |
| Big Brown - Venus Switch | Watermill - Cedar Hill Switch | 8 |
| Marion - Hill Country/Skyline | Cibolo - Schertz | 8 |
| Midkiff - Sprayberry | Crane - Crane Arco | 6 |
| Enterprise - Trinidad/Martin Lake | Martin Lake - Tricorner | 5 |
| West Levee - Watermill | Cedar Hill - Watermill | 5 |
| South - North CSC |  | 5 |
| Morgan Creek - Odessa | Odessa - Big Three | 4 |
| Benbrook -Parker/Graham | Stephenville - Lingleville | 4 |
| Odessa Switch - Moss | Moss Switch - Amaco N Cowden Tap | 4 |
| Cedar Hill Tr | Venus - Everman | 4 |
| Rio Hondo - La Palma | Rio Hondo - La Palma | 4 |
| Uvalde - Hamilton | Asherton - West Conoco | 4 |
| STP - Whitepoint | Blessing - Lolita | 3 |
| Clear Springs - Marion/Zorn | SMI - McQueeney | 3 |
| North - Houston CSC |  | 3 |
| N McCallen - N Edinburg | N Edinburg - Moore Field | 3 |
| Kirkland Park - North Haven | Central Expressway - Kirkland Park | 3 |
| West Levee Tr | Compton Road - Industrial Bvd | 3 |
| Caddo Switch - Heights | Amoco - Terminal Switch | 2 |
| Enterprise - Stryker Creek | Trinidad - Martin Lake | 2 |
| Calaveras- Skyline/Walzem Rd | Calaveras - Ball Park | 2 |
| Indian Mesa - Mesa View | Air Products - W Yates | 2 |
| Crane - Midkiff | Crane - Crane Arco | 2 |
| West Levee - Watermill | Watermill Tr | 2 |
| Northeast - North CSC |  | 2 |
| Duke - Aderhold | Duke - SE Edinburg | 2 |
| N McCallen - Frontera | Bates Tr | 2 |
| Oklaunion - Fisher Road | Vernon Tr | 2 |
| Clear Springs - Marion/Zorn | McQueeny - Cibolo | 2 |
| N Edinburg - Rio Hondo | S McCallen - Las Milpas | 2 |
| Bates - Frontera | N Edinburg - Moore Field | 2 |
| San Angelo - Menard | Ballinger - Paint Rock | 2 |
| Contingency | Overload | Occurrences |
| Zorn - Lytton Springs/Austrop | Flatonia Tr | 1 |
| Midland East - Odessa | Odessa - Southwest | 1 |
|  | Cedar Bayou Tr | 1 |
| Austrop - Sandow | Austrop Tr | 1 |
| Roanoke - Parker | Benbrook - Calmont | 1 |
| Comanche Peak - Decordova/Wolf Hollow - Rocky Creek | Johnson Switch - Venus Switch | 1 |
| Renner Tr | North Haven - Alpha Road | 1 |
| Allen Renner/Tennyson | Plano Parker - Allen Switch | 1 |
| Cedar Hill Tr | West Levee Tr 2 | 1 |
| Asherton - Eagle Pass | Uvalde - Hamilton | 1 |
| Elkton - Tyler | Stryker Creek - Troup | 1 |
| Military Highway - Midtown | Loma Alta Tr | 1 |
|  | Crane - Crane Arco | 1 |
| West Yates - Mesa View | Air Products - W Yates | 1 |
| Elkton - Martin Lake | Stryker Creek - Troup | 1 |
| Dilley Switch - Sam Miguel | Derbys - Pearsall | 1 |
| Duke - N Edinburg | Polk - Hall Acres | 1 |
| Venus - Everman | Venus - Everman | 1 |
| Allen Switch - Royse Switch/Monticello | Edgemere - Central Expressway | 1 |
| Military Highway - La Palma | Lapalma - Cavasos | 1 |
| N McCallen - N Edinburg | Duke - SE Edinburg | 1 |
| Fort Stockton Tr | Rio Pecos Tr | 1 |
| Big Lake Tr | McCamey - Rankin | 1 |
| Temple - Lake Creek/Tradinghouse | Lake Creek - Temple | 1 |

New Procedures/ Forms/ Operations Bulletins

Power Operations Bulletins 82 – 92

- Modified section 2.9 to include handling Inadvertent Payback (Frequency).

- Updated the first bullet in section 3.5 Appendix 4 stating that during the months of April, May or October for hours that the forecasted load will be within 85% (was 80%) of forecasted peak load for the operating day the (Day Ahead).

- Added new section 2.1.3 to address initial synchronization of new resources (Supervisor).

- Revision for consistent process for OC1 changes needed to support outages.  Also changed verbiage in section 2.2.1 from a constraint to a CSC (Transmission).

- Clarification for section 2.5.3 “Operator Instructions for High Frequency” (Frequency).

- Section 2.2.1 “Monitoring Outages” added back in procedure, existing 2.2.1 moved to new section 2.2.2 “OC1 Limits for Outage Support”.  (Transmission).

- EECP Load Shed Table updated in the Operating Guides section 4.5.3.

89-90	Added new section 2.6.4 “Notification of Condition Termination” (Frequency&Transmission).

- Verbiage modified in the first note under “Operator Instructions for High Frequency” concerning the Frequency Control Desk Operator may (was must) consult with the T&S desk to confirm that no OOMs from that desk could be affecting frequency (Frequency).

- TC#228 extending TC#112 regarding interrupted outages due to computer software program unable to execute procedure.

# Security Alert Stage/ Threatcon/ Related issues

Security Threat Alert Yellow (Elevated) maintained through May.

OCN, Advisory, Alert, Emergency Notice and Major Events

5/1  10:11-14:00	OCN issued for severe weather in Houston Area.

5/8  15:58–05/09 2:04	Alert issued for 69kV Amoco to Terminal Switch.

5/11 15:00-21:00	OCN issued in the Houston Zone for severe weather.

5/12 10:23-12:00	Transmission Alert issued for Allen Sw – Shilo Rd 138 line.

5/19 15:30-22:00	Alert – Post Contingency loading on West Levee Auto #2

5/27 15:30-24:00	Alert issued for North McAllen – North Edinburg.

# Communication

# 5/2    Held 01:00 interval.  CSC Constraint activated when it should not have.

5/4   07:45 – 08:30   Portal not functioning.

5/11  Held 18:15 interval.  OOME and significant Resource Plan Changes caused a bad offset

Calculation.

ERCOT peak (Unofficial)

5/31 17:00	48,743

## Max Temperature

5/30&5/31	104.5  Far West