March 31, 2004

Attachment A-1, Jacksboro to West Denton

History

Many factors support the justification of the construction of the Jacksboro to West Denton 345 kV circuit. First and foremost, it is to maintain the ERCOT transmission system within the planning criteria as defined in section 7 of the ERCOT Operating Guides. The new circuit will eliminate several overloads and low voltage conditions during contingencies in the Northwest DFW metroplex. Other factors included in the analysis:

- Metroplex generation dispatch.

- Continued high load growth on the north side of the Metroplex.

- Load growth in areas in and surrounding Denton and Decatur.

- New generation installed northwest of Ft. Worth.

- Export of generation resources from West Texas.

- Existence of only one 345 kV path from west to east on the north side of Ft. Worth.

- Parker Switching Station as a security issue.

Proposed Transmission Upgrades

The Jacksboro - West Denton 345-kV Project will involve construction of an approximate 50-mile double-circuit 345 kV line using 2-1590 kcmil ACSR conductor with one circuit in place from Oncor’s Jacksboro Switching Station to TMPA’s West Denton 345/138-kV Switching Station. One 345-kV breaker will be installed at Jacksboro Switching Station and three 345-kV breakers will be installed at West Denton to terminate this line. Estimated cost of this proposal is $46,470,000.

This project is presently planned to be in service by May of 2006.

ERCOT Staff Independent Analysis

Oncor recommended that a 4-ohm 138-kV series reactor be installed on the low side of the West Denton 345/138-kV autotransformer in this project. This prevents the power flowing through the autotransformer from exceeding its emergency rating under certain 345-kV contingencies. ERCOT recommended that a separate analysis should be done, at some point, to determine the course of action that should be pursued to increase 345/138-kV autotransformer capacity in the Denton area. TMPA has performed studies and is already investigating the improvement to the transmission system by installing a second 345/138-kV autotransformer at West Denton. Either the Oncor or the ERCOT recommendation will be a part of this project.

ERCOT also requested that a review should be made of the proposed line construction to determine if there is sufficient ampacity and flexibility to meet ERCOT’S requirements for the foreseeable future. This review should include an economic analysis of installing a conductor with a higher MVA rating.

Request for Comments

This material was distributed via email on August 27th, Tractabel comments on September 17th, Oncor response to Tractabel comments on November 6th, discussed at the December 11th meeting, and posted on the ERCOT website.  Comments were requested on the project at the meeting.  A final ERCOT Staff recommendation released at via email to the North RPG on January 21, 2004.

Other Alternatives Considered

Alternative 1 - Construction of a 345 kV line from Willow Creek to West Denton.   This alternative consists of a double-circuit line with one circuit in place using 2-1590 kcmil ACSR and would be approximately 40 miles in length.   A series 138 kV series reactor installed at West Denton is also required.   This alternative would perform comparably to the proposed project in the near term.   However, this alternative is not being pursued because it places a 21-mile section of single-circuit construction utilizing 2-795 kcmil ACSR conductor in the newly completed path from Graham to West Denton; which is otherwise double-circuit construction utilizing 2-1590 ACSR conductor.   This section will overload under contingency with higher west to north transfers and/or with generation added in the Wichita Falls area.   The cost difference between this alternative and the proposed line is canceled by the cost savings that were realized in 2002 when the first section of this path to West Denton was built into Jacksboro instead of Willow Creek.  A rough cost estimate for Alternative 1 is $38,220,000.

Alternative 2 – No new 345 kV construction.   Rebuild and upgrade existing 345 kV and 138 kV transmission facilities.   This will include:

- Rebuilding the Willow Creek – Parker 345 kV line (17.2 miles, double-circuit construction, with one circuit of 2-1590 kcmil ACSR conductor in place).

- Rebuilding the Parker – Benbrook 345 kV line (18.7 miles, double circuit construction, both circuits, 2-1590 kcmil ACSR conductor).

- Accelerating the upgrade of the Wolf Hollow – Rocky Creek 345 kV line by one to two years (35.7 miles, double-circuit construction, both circuits, 2-1590 kcmil ACSR conductor).

- Installation of 300 MVAR of 138 kV capacitors (100 MVAR each at Eagle Mountain, Roanoke, and West Denton).

- Installation of a 2-ohm 138 kV series reactor at Eagle Mountain on the low side of the 345/138 kV autotransformer.

- Rebuilding the Sherry – General Motors - Great Southwest 138 kV line sections (2.4 miles, double circuit construction, both circuits, 2-1033 kcmil ACSR conductor).

- Rebuilding the Calmont – Carswell – Blackstone 138 kV line sections (5.3 miles, double-circuit construction, with one circuit of 2-1033 kcmil ACSR conductor).

- Rebuilding the Calmont – Western Hills 138 kV line (2.6 miles, double circuit construction, both circuits, 2-1033 kcmil ACSR conductor).

This alternative was not pursued because it does not provide the 345 kV infrastructure necessary to move increasing amounts of power to and around the north side of the metroplex, it does not provide the 345 kV infrastructure necessary to serve the large amount of load that will develop north of Tarrant County, it does not significantly improve flexibility in generation dispatch, and it leaves Parker Switching Station as a critical node for system security.   This alternative does not provide the benefits into the future that the proposed line will provide.   Alternative 2 is estimated to cost in excess of $52,000,000.

ERCOT Staff Recommendation

ERCOT Staff recommends that the Board approve the construction of the Jacksboro to West Denton 345 kV line projects as outlined above.