## Slide 1: POWER SYSTEM PLANNING CHARTER AND PROCESSES Presentation to TAC May 6, 2004
Transmission Services
Ken Donohoo, Manager of System Planning
Dan Woodfin, Manager of Resource Planning
www.ercot.com

## Slide 2: CURRENT MAJOR STUDIES UNDERWAY
Central Texas (Clear Springs-Salado 345 kV Line)
  North and Central RPG
  Underway, expect completion Fall 2004
Dallas-Ft. Worth and Northeast ERCOT
  North RPG
  Scope developed, reviewed and approved
  Underway, expect completion Winter 2004-2005
Rio Grande Valley Area (Laredo-McAllen-Harlingen-Brownsville)
  South RPG and RMRTF
Bryan-College Station Area
  North and South RPG
  Just starting

## Slide 3: CHARTER DEVELOPMENT PROCESS
DEVELOPED AND REVIEWED WITH:
  Regional Planning Groups (North, South & West)
  Transmission Owners (TDSP’s)
  PUCT Staff
  Market Participants and other Stakeholders
PRESENTED AND ACCEPTED BY ROS
  September 10, 2003
PRESENTED AND ACCEPTED BY WMS
  September 17, 2003
PRESENTED AND ACCEPTED BY TAC
  October 9, 2003
PRESENTED AND ACCEPTED BY ERCOT BOARD
  October 22, 2003

## Slide 4: PLANNING RESPONSIBILITIES
CHARTER DEFINES PLANNING RESPONSIBILITIES FOR:
ERCOT STAFF
TDSP’s (Transmission Owners)
STAKEHOLDER/MARKET PARTICIPANTS
PUBLIC UTILITY COMMISSION
  Substantive Rules
REGIONAL PLANNING GROUPS

## Slide 5: PLANNING PROCESS
Studies include computer modeling of the generation, transmission facilities and station loads
Apply contingency conditions along with changes in load and generation that might be expected to occur
Identify adverse results based upon the planning criteria
Develop options and examine the effectiveness of various problem-solving alternatives
  Test effectiveness of each grid configuration and facility change
  Thermal and Voltage Limits (Steady State)
  Dynamic Stability Limits (Transient and Voltage)
Repeated simulations under different conditions are required
Options considered may affect other alternatives so that several different combinations must be evaluated
Once feasible alternatives have been identified, the process is continued with a comparison of those alternatives, multiplying the number of simulations required
To determine the most viable, compare the short-range and long-range benefits of each including operating flexibility, maintenance/construction coordination and compatibility with future plans

## Slide 6: REGIONAL PLANNING GROUPS
Goal is to obtain all viewpoints and ideas and avoid problems due to lack of communication
For Major Project Studies before project development stakeholder input requested at:
  Study scope development – start of study
  Preliminary status at middle of study
  Presentation of preliminary report at end of study
Web posting and emails to RPG members are “Official Notice”
System Planning data area on Internet
  http://www.ercot.com/tmaps/Login.cfm
  Must register for access
Email exploder lists for each region (North, South & West)
  http://lists.ercot.com
  Open, anyone can be on the lists
Regional Planning Group email addresses
  North – regplangroupnorth@lists.ercot.com
  South – regplangroupsouth@lists.ercot.com
  West – regplangroupwest@lists.ercot.com

## Slide 7: PLANNING PROCESS Project Submission And Review Requirements
Small Projects - “Tier 1”
  138 kV to 60 kV projects not requiring PUCT certification (CCN)
  Regional Planning Group review (includes ERCOT & PUCT Staff)
Large Projects - “Tier 2”
  345 kV and higher projects along with other projects requiring PUCT certification (CCN)
    Includes exempt municipal & electric cooperatives projects under what-if test
  Regional Planning Group review (includes ERCOT & PUCT Staff)
  ERCOT Staff independent study
Why haven’t all projects been submitted for RPG review?
  Open process phase-in issue
  Propose that we require all projects with in-service date of 2006 or greater be submitted for review
    2004, 2005 and some 2006 projects are already in-progress
    Many 345 kV projects for 2004 through 2010 have already be submitted, reviewed and are underway

## Slide 8: PLANNING PROCESS Generation New Interconnection or Change
ERCOT Security Screening Study
  Site feasibility for new interconnection or change (addition)
  Identify current operating limits
  Rough estimate of the transmission system additions needed to integrate all of the new or changed generation
  “ERCOT will inform the generating entity if it considers the proposed site to be inappropriate to the point that ERCOT will not support the addition of transmission needed to integrate the project into the transmission system.”
    Highly subjective
Full Interconnection Study with transmission owners
  Completes interconnection or change request
Complete Interconnection Agreement with transmission owner
  New generation project or change becomes public
  Impact studies (security and full interconnection) posted on internet
  Generation related transmission projects submitted to the full Regional Planning Group for review and approval

## Slide 9: PLANNING CRITERIA
ERCOT Planning Criteria state the fundamental minimum requirements for planning and constructing reliable interconnected electric systems under:
  Normal Condition
    PC Category A
  Single Contingency Conditions
    PC Category B
    Includes the contingency loss of single faults resulting in multiple elements (SFME) out
    Includes the contingency loss of a double-circuit transmission line that exceeds 0.5 miles in length
      Double circuit = Single contingency = Category B
    Includes the contingency loss of any single generating unit unavailable, and with any other generation preemptively redispatched, the contingency loss of a single transmission element
      Generator + Single contingency = Category B
  Multiple contingency conditions
    PC Category C & D
    Allows generation, load and/or system adjustment

## Slide 10: TYPES OF PROJECTS
Reliability Driven Projects are defined as system improvements primarily intended to resolve current or projected levels of reliability criteria violations that cannot be met by redispatch of existing generation
Economic Projects are defined as system improvements primarily intended to resolve current or projected levels of reliability criteria violations that could instead be solved by preemptive redispatch of existing generation but have been initiated because they are projected to result in a net economic benefit to the market based on ERCOT-wide impacts.

## Slide 11
Reliability | Economic
Study on-peak and off-peak load conditions | Study all hours
Use unconstrained economic dispatch powerflow case Solve category B criteria violations through preemptive redispatch | Use security-constrained economic dispatch for each hour
Identify remaining criteria violations | Identify elements that result in less than economic dispatch through time
Develop upgrades that minimize cost of solving remaining criteria violations through time | Develop upgrades that minimize sum of construction and production cost through time
May plan reliablity-driven project for criteria violation in one hour | May not plan upgrade that would result in reduced congestion in peak hours if not warranted by cost reductions over time
PROJECT DRIVERS
Notes: <number>
<footer>
<header>
<date/time>

## Slide 12: Economic Criteria
The criteria for determining whether a project is economic is the increase in economic value to the market due to the project, as measured by an expected reduction in the market production cost due to the project that exceeds the cost of the project.

## Slide 13: DFW/NE Study Process Overview
List of Highest Congestion Cost Elements
Peak Hour Contingency Analysis
Develop Reliability-driven Solutions
Economic Evaluation of Sets of Alternatives
Recommend Upgrades
Powerflow Cases with Unconstrained Economic Dispatch
Violations Solved by Redispatch?
Develop Solution Alternatives to Overloads
Contingency Analysis of Economic Alternatives
No
Yes
List of Overloads with No Feasible Redispatch Solutions
Notes: <number>
<footer>
<header>
<date/time>

## Slide 14: QUESTIONS/DISCUSSION

## Slide 15: PLANNING CRITERIA Category A & B

## Slide 16: PLANNING CRITERIA Category B
The contingency loss of a double-circuit transmission line that exceeds 0.5 miles in length (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal should not cause a) cascading or uncontrolled outages, b) instability of generating units at multiple plant locations, or c) interruption of service to firm demand or generation other than that isolated by the double-circuit loss, following the execution of all automatic operating actions such as relaying and special protection systems. Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., Remedial Action Plans), such as generation schedule changes or curtailment of interruptible load, should not result in applicable voltage or thermal ratings being exceeded.
2. With any single generating unit unavailable, and with any other generation preemptively redispatched, the contingency loss of a single transmission element (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal should not cause a) cascading or uncontrolled outages, b) instability of generating units at multiple plant locations, or c) interruption of service to firm demand or generation other than that isolated by the transmission element, following the execution of all automatic operating actions such as relaying and special protection systems. Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., Remedial Action Plans) such as generation schedule changes or curtailment of interruptible load, should not result in applicable voltage or thermal ratings being exceeded.
Generator + Single contingency = Category B
Double circuit = Single contingency = Category B

## Slide 17: PLANNING CRITERIA Category C

## Slide 18: PLANNING CRITERIA Category D

## Slide 19: PLANNING CRITERIA
Footnotes to Table
a) Applicable rating (A/R) refers to the applicable normal and emergency facility thermal rating or system voltage limit as determined and consistently applied by the system or facility owner.
b) Planned or controlled interruption of generators or electric supply to radial customers or some local network customers, connected to or supplied by the faulted component or by the affected area, may occur in certain areas without impacting the overall security of the interconnected transmission systems. To prepare for the next contingency, system adjustments are permitted, including curtailments of contracted firm (non-recallable reserved) electric power transfers.
c) Cascading is the uncontrolled successive loss of system elements triggered by an incident at any location. Cascading results in widespread service interruption, which cannot be restrained, from sequentially spreading beyond an area predetermined by appropriate studies.
d) Depending on system design and expected system impacts, the controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, or the curtailment of contracted firm (non-recallable reserved) electric power transfers may be necessary to maintain the overall security of the interconnected transmission systems.
e) A number of extreme contingencies that are listed under Category D and judged to be critical by the transmission planning entity(ies) will be selected for evaluation. It is not expected that all possible facility outages under each listed contingency of Category D will be evaluated.