| OGRR Number | 149OGRR | OGRR Title | Types Of Responsive Reserve |
| --- | --- | --- | --- |
| Operating Guide Section Requiring Revision |  | 2.5.2.3, Types of Responsive Reserve |  |
| Protocol Section Requiring Revision, if any. |  | ## PRR502 Aggregation of Combined Cycle Units Providing RRS (approved by BOD on 6/15/04) |  |
| Effective Date |  | September 1, 2004 |  |
| Revision Description |  | Allows Combined Cycle Units operating a CT or GT coupled to a Steam Turbine to be considered as one unit by ERCOT, by aggregating the CT or GT and Steam Turbine net maximum capability to calculate the 20% compliance capability to provide Responsive Reserve. |  |
| ###### Benefit |  | Combined Cycle Plants operate in an interdependent manner. Responsive Reserve awarded to a single unit in a block will be met by the capacity of all units in the block in reality. The current Ancillary Services auction process does not accommodate awards to the units to follow actual operations. |  |
| OWG Recommendation |  | OWG recommends approval of OGRR149 as revised by OGRTF Comments. |  |
| ROS Recommendation |  | ROS recommends approval of OGRR149 as recommended by OWG. |  |
| PRS Consistency Determination |  | No PRS member noted a discrepancy between OGRR149 and the Protocols. |  |
| TAC Action |  | TAC approved OGRR149 as recommended by ROS. |  |

| Sponsor |  |
| --- | --- |
| Name | Stephen C. Knapp |
| E-mail Address | Steve.knapp@constellation.com |
| Company | Constellation Power Source, Inc. |
| Company Address | 111 Market Place, Suite 500, Baltimore, Maryland 21202 |
| Phone Number | (410) 468-3606 |
| Fax Number | (410) 468-3540 |

Proposed Operating Guide Language Revision

#### 2.5.2.3	Types Of Responsive Reserve

Reference:  Protocols Section 6.5.4, Responsive Reserve Service

Responsive Reserve Service (RRS) may be provided by:  (a) Unloaded Generation Resources that are On-line; (b) Resources controlled by high-set under-frequency relays; (c) Hydro Responsive Reserves; or (d) From DC Tie response that stops frequency decay.  The minimum amount of RRS provided by Generation Resources shall be as specified in the Operating Guides.  QSE’s Generation Resources providing RRS must be On-line and capable of ramping to the awarded output level within ten (10) minutes of the notice to deploy energy, must be immediately responsive to system frequency, and must be able to maintain the scheduled level for the period of service commitment.  The amount of RRS on an individual Generation Resource may be further limited by requirements of the Operating Guides.

Responsive reserves provided by a QSE shall meet the following requirements:

- (1)	In no case shall more than twenty percent (20%) of the Net Dependable Capability for any non-Combined Cycle thermal unit be used as Responsive Reserve.

- (2)	In no case shall more than twenty percent (20%) of the combined Net Dependable Capability for any Combined Cycle Block with one or more CTs or GTs coupled to a Steam Turbine, with their net maximum capability aggregated together, be used as Responsive Reserve.

- (3)	In no case shall more than twenty percent (20%) of the Net Dependable Capability for any hydro unit with a five percent (5%) droop setting operating as a generator be used as Responsive Reserve.