| OGRR Number | 150OGRR | OGRR Title | Clarification to UF Relay Trip Time for Load Shedding |
| --- | --- | --- | --- |
| ###### Date |  | 8/13/04 |  |
| ## Submitter’s Information |  |  |  |
| Name |  | Wayne Kemper |  |
| E-mail Address |  | Wayne.kemper@CenterPointEnergy.com |  |
| Company |  | CenterPoint Energy |  |
| Company Address |  | PO Box 1700 Houston, TX 77251 |  |
| Phone Number |  | 713-207-2192 |  |
| Fax Number |  | 713-207-2444 |  |

Comments

The changes recommended by the SPWG are acceptable to CenterPoint Energy with the exception that the time delay of “30 cycles” for frequency measuring relays should be changed to “no more than 30 cycles”.  The TDSP must have the flexibility to shorten the relay trip time in order to meet the overall goal of interrupting in no more than 40 cycles.

Revised Proposed Operating Guide Language

Automatic firm Load shedding will be initiated as follows:

Frequency 		% Load Relief

59.3 Hz			 5%

58.9 Hz			10%

58.5 Hz			10%

Load shedding will be widely dispersed in each TDSP, with no regard for the REP, and will be accomplished by using high-speed under-frequency relays The frequency measuring relays shall have a time delay of no more than 30 cycles (or 0.5 seconds for relays that do not count cycles). If the frequency and time values are reached, an irretrievable trip is initiated. Total time from the time frequency first reaches one of the values specified above to the time load is interrupted should be no more than 40 cycles, including all relay and breaker operating times.   If the frequency drops below 58.5 Hz, each TDSP must determine additional steps it will take to survive.  Under-frequency relays may be installed on transmission facilities under the direction of ERCOT, provided the relays are set at 58.0 cycles or below, are not directional, and have at least 2.0 seconds time delay.  Load restoration will be under the direction of the ERCOT Control Area Authority.  A TDSP may by mutual agreement, with the approval of the TAC, arrange to have all or part of its automatic Load shedding obligation carried by another TDSP.  ERCOT will be notified and provided with the details of any such arrangement prior to implementation