| OGRR Number | 150OGRR | OGRR Title | Clarification to UF Relay Trip Time for Load Shedding |
| --- | --- | --- | --- |
| ###### Date |  | 8/17/04 |  |
| ## Submitter’s Information |  |  |  |
| Name |  | Ed Echols on behalf of Demand Side Working Group |  |
| E-mail Address |  | Ed.echols@txu.com |  |
| Company |  | TXU Energy |  |
| Company Address |  | 1717 Main, Dallas TX |  |
| Phone Number |  | 214 875 8070 |  |
| Fax Number |  | 214 875 9052 |  |

Comments

The DSWG suggests that the reference to “REP” be replaced with “LSE” to ensure that it continues to be clear that all customers are subject to being interrupted during load shedding events.  Further, no preference should be made to any customer based on the entity that serves customers whether in the competitive market or in an area where customer choice is not in place.

This change are noted (highlighted in yellow) below to the original OGRR.

Revised Proposed Operating Guide Language

Automatic firm Load shedding will be initiated as follows:

Frequency 		% Load Relief

59.3 Hz			 5%

58.9 Hz			10%

58.5 Hz			10%

Load shedding will be widely dispersed in each TDSP, with no regard for the LSE, and will be accomplished by using high-speed under-frequency relays….NO OTHER Suggested changes to the proposed PRR by DSWG.