## ERCOT Operations Report

## ROS & OWG

## July 2004

July Frequency control   59.9 > F > 60.1

7/1  00:03	59.893	  ERCOT SCE = -217 and a 100 MW resource was lost.

- 1300 MW schedule change, -740 MW Largest individual change.

7/19  02:20	60.172   POS system unavailable from 01:22 until 01:55.  Frequency

control and Short-Term Load Forecast were unavailable

during this time contributing to a high frequency event .

Disturbances

|  | July Trips | MW Lost |
| --- | --- | --- |
| 7/4/2004 16:30 | 59.899 | 400 MW |
| 7/13/2004 13:39 | 59.877 | 600 MW |
| 7/22/2004 11:08 | 59.872 | 750 MW (4 units) |
| 7/24/2004 11:06 | 59.856 | 600 MW |
| 7/30/2004 11:05 | 59.838 | 615 MW |
| 7/30/2004 11:30 | 59.830 | 665 MW (3 units) |

Deployed Responsive   (17)

7/1	08:02

7/4	03:35		22:04

7/5	10:18

7/9	09:02

7/11	06:36

7/13	22:01

7/16	22:02

7/19	02:35

7/24	00:02

# Locations and Relative Activity of Congestion Management

| Historical | July '03 | June '04 | July '04 |
| --- | --- | --- | --- |
| DFW | 401 | 226 | 324 |
| E RIO | 134 | 120 | 108 |
| W RIO | 33 | 60 | 59 |
| Laredo | 91 | 79 | 91 |
| Rio Pecos | 48 | 0 | 0 |
| Corpus | 32 | 30 | 31 |
| Abilene | 41 | 29 | 31 |
| San Angelo | 32 | 30 | 31 |
| Western | 15 | 36 | 6 |
| Houston | 1 | 0 | 2 |
| San Antonio | 1 | 2 | 0 |
|  | 830 | 612 | 686 |

| Contingency | Overload | Occurrences |
| --- | --- | --- |
| N McCallen - N Edinburg | Polk - Hall Acres | 25 |
| Austrop - Sandow | Austrop Tr | 25 |
| South - Houston CSC |  | 22 |
| Marion - Hill Country/Skyline | Cibolo - Schertz | 16 |
| Gibbons Creek - East | Gibbons Creek - Greens Prarie | 15 |
| West Levee Tr | Compton Road - Industrial Bvd | 14 |
| N McCallen - N Edinburg | Pharr - Pharr MVEC | 14 |
| La Palma - Rio Hondo | La Palma - Rio Hondo | 12 |
| Gibbons Creek - Twin Oaks Switch | Jewet - Watsons Chapel | 11 |
| Frontera - S McCallen | Polk - Hall Acres | 11 |
| Clear Springs - Marion/Zorn | SMI - McQueeney | 11 |
| Big Lake - N McCamey | Fort Lancaster - Illinois 4 | 11 |
| Valley Tr 1 | Paris Sw - Kimberly Clark | 8 |
| Uvalde - Hamilton | Asherton - West Conoco | 8 |
| Buda - Turnerville | Marshall Ford - Hicross | 6 |
| SA Red Creek Tr 2 | SA Red Creek Tr 1 | 5 |
| Mulberry Creek W Tr. | Mulberry Creek E Tr. | 5 |
| Temple - Lake Creek/Tradinghouse | Robertson - Milano | 4 |
| North - Houston CSC |  | 4 |
| N McCallen - N Edinburg | Polk - Pharr | 4 |
| Comanche Peak - Decordova/Wolf Hollow - Rocky Creek | Johnson Switch - Venus Switch | 4 |
| Cagnon - Marbach | Medical Center - Bandera | 4 |
| Big Lake Tr | Fort Lancaster - Illinois 4 | 4 |
| Sandow Tr. | Robertson - Milano | 3 |
| Northeast - North CSC |  | 3 |
| Mt Enterprise - Trinidad / Martin Lake - Stryker Creek | Nacogdoches - N Herty | 3 |
| West Levee - Watermill | Cedar Hill - Watermill | 2 |
| Temple - Lake Creek/Tradinghouse | Lake Creek - Temple | 2 |
| South - North CSC |  | 2 |
| San Angelo - San Angelo North | San Angelo Concho Tr | 2 |
| San Angelo - Menard | Ballinger - Paint Rock | 2 |
| Roanoke Sw Tr | Bedford - Euless | 2 |
| Polk - Hall Acres |  | 2 |
| N Denton - W Denton | N Sanger - Spring | 2 |
| Morgan Creek - Odessa | Big Spring Switch - Big Spring West | 2 |
| Lon Hill Tr 2 | Lon Hill Tr 1 | 2 |
| Live Oak - Sonora | El Dorado | 2 |
| Lapalma 38/69 1 | Lapalma 38/69 2 | 2 |
| Cagnon - Marbach | Five Points - West Side | 2 |
| Big Lake - N McCamey | McCamey - Rankin | 2 |
| Big Brown - Richland Chambers | Tricorner - Watermill | 2 |
| Bates - Garza | Freer - San Diego | 2 |

| Contingency | Overload | Occurrences |
| --- | --- | --- |
| West Levee - Watermill | Southerland - Sargent Road | 1 |
| West Levee - Sargent Rd | Cedar Hill - Watermill | 1 |
| Valley Tr 1 |  | 1 |
| Sargent - Watermill | Cedar Hill - Watermill | 1 |
| Sargent - Watermill | Seagoville Sw - Lawson Rd | 1 |
| Sandow Tr. |  | 1 |
| San Miguel - Pearsall | Derbys - Pearsall | 1 |
| San Angelo Live Oaks | San Angelo Concho - Lake Nasworthy | 1 |
| SA Red Creek - SA North | SA Red Creek Tr 1 | 1 |
| Roanoke - Parker | Hanley - Randol Mill East Tap | 1 |
| Polk - Pharr | McColl Rd - McCallen | 1 |
| Polk - Hall Acres | Pharr - Pharr MVEC | 1 |
| Nueces Bay - Whitepoint | Nueces Bay - Whitepoint | 1 |
| N McCamey - Rio Pecos | McCamey - Rankin | 1 |
| Midland East - Odessa | Odessa - Big Three | 1 |
| Lon Hill Tr 1 | Warburton - Victoria | 1 |
| Lon Hill - Whitepoint | Lon Hill Tr 1 | 1 |
| Laredo - Falfurrias | Laredo - Freer | 1 |
| Lake Creek - Jewett | Navarro - Richland Chambers | 1 |
| La Palma - Rio Hondo | Raymondville Tr | 1 |
| Killeen Sw Tr | Harker Heights - Belton | 1 |
| Jewett Tr | Stryker Creek - Dialville | 1 |
| Gibbons Creek - Roans Prarie | Jewet - Watsons Chapel | 1 |
| Forney Tr | Seagoville Sw - Lawson Rd | 1 |
| Duke - Aderhold | Polk - Hall Acres | 1 |
| Dilley Switch - San Miguel | Pleasonton - Jourdanton | 1 |
| Benbrook Sw - Calmont | Benbrook Sw - Calmont | 1 |
| Austrop Tr | Robertson - Milano | 1 |
| Austrop - Lost Pines | Winchester - Fayetteville | 1 |
| Atkins Tr | Atkins - Briarcrest | 1 |
| Asherton - W Conaco |  | 1 |
| Asherton - Eagle Pass | Uvalde - Asphalt Mines | 1 |

Indicates a Remedial action plan has been developed for the element

# New RAP/SPS

7/1	Medical Center – Bandera Road Pre-Contingency Action Plan

7/12	Hicross – Marshall Ford Pre-Contingency Action Plan

7/14	Milano Robertson Pre-Contingency Action Plan

The above have been generated due to transmission outages or maintenance in the area.

7/28 	Lake Creek – Jewett Mitigation Plan

New Procedures/ Forms/ Operations Bulletins

| Date | Power Operations Bulletin | Subject |
| --- | --- | --- |
| 07/27/2004 | ERCOT Power Operations Bulletin 104 | Frequency Control Desk V2R13 - CN#143 |
| 07/15/2004 | ERCOT Power Operations Bulletin 103 | Transmission & Security Desk V2R23 - CN#142 |
| 07/12/2004 | ERCOT Power Operations Bulletin 102 | Shift Supervisor V2R8 - CN#140 |
| 07/12/2004 | ERCOT Power Operations Bulletin 101 | Day Ahead Desk - V2R14, CN#141 |
| 07/01/2004 | ERCOT Power Operations Bulletin 100 | Verbal Dispatch Exception - Frequency Control Desk |
| 07/07/2004 | ERCOT Power Operations Bulletin 99 | Verbal Dispatch Exception - Tranmsission & Security Desk |
| 07/01/2004 | ERCOT Power Operations Bulletin 98 | Transmission & Security Desk V2R23 - CN#136 |
| 07/01/2004 | ERCOT Power Operations Bulletin 97 | Shift Supervisor V2R8 - CN#135 |
| 07/01/2004 | ERCOT Power Operations Bulletin 96 | Transmission & Security Desk V2R23 - CN#134 |
| 07/01/2004 | ERCOT Power Operations Bulletin 95 | Shift Supervisor V2R8 - CN#132 |

95 & 96– Placing units in test mode.

97 – NERC/DOE disturbance reporting.

98 – Remedial Action Plans

99 & 100 – Issuing VDE’s for intervals where the OOME instruction was not included in the MCE

execution.

101 -   Clarifications to the Day – Ahead process

102 -   Placing units in test mode.

103 -   Mitigation Plans.

104 -   Actions when frequency telemetry is incorrect.

# Security Alert Stage/ Threatcon/ Related issues

Security Threat Alert Yellow (Elevated) maintained through June.

Major system voltage problems

None

Blackout/Load Shed incidences

7/19  16:00 – 19:00	75 – 100 MW load reduction at the Sandow station to relieve loading on

Sandow 345/138 kV Tr, Robertson – Milano 138 kV line, and Jewet – Watsons Chapel 138 kV line.

OCN, Advisory, Alert, Emergency Notice and Major Events

| 7/1 | 16:00-22:30 | Transmission Alert issued. |
| --- | --- | --- |
|  |  | Loss of double Austrop - Sandow loads Hicross - Marshall Ford 138 kV. |
|  | 16:00-22:30 | Transmission Alert issued. |
|  |  | Loss of Glidden (LCRA) - Glidden (CSW) loads Blessing - Midfield 69 kV. |
| 7/2 | 13:40 -23:55 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
|  | 13:53 -18:00 | Transmission Alert issued. |
|  |  | Loss of Glidden (LCRA) - Glidden (CSW) loads Blessing - Midfield 69 kV. |
| 7/3 | 14:00 -21:00 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
| 7/5 | 17:25-22:35 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
| 7/6 | 14:30 - 20:45 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
| 7/7 | 15:30 - 23:40 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
| 7/8 | 16:30 - 24:00 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
| 7/9 | 12:00 -24:00 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
|  | 13:45-24:00 | Transmission Alert issued. |
|  |  | Loss of Dilley - San Miguel loads Pleasanton - Jourdanton 69 kV. |
|  | 16:00-24:00 | Transmission Alert issued. |
|  |  | Loss of Lon Hill 138/69 kV Tr 2 loads Lon Hill 138/69 kV Tr 1 |
| 7/10 | 13:00-24:00 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
|  | 17:30-18:30 | Transmission Alert issued. |
|  |  | Loss of Gibbons Creek - Greens Prarie loads Gibbons Creek - East 138 kV. |
| 7/11 | 14:30-19:00 | Transmission Alert issued. |
|  |  | Loss of North McCallen - North Edinburgh loads Polk - Hall Acres. |
| 7/12 | 14:00-23:00 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
| 7/13 | 13:00-24:00 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
|  | 15:40-24:00 | Transmission Alert issued. |
|  |  | Loss of Gibbons Creek - Greens Prarie loads Gibbons Creek - East 138 kV. |

| 7/14 | 11:50-22:40 | Transmission Alert issued. |
| --- | --- | --- |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
|  | 15:00-22:00 | Transmission Alert issued. |
|  |  | Loss of Gibbons Creek - Greens Prarie loads Gibbons Creek - East 138 kV. |
|  | 15:45-22:00 | Transmission Alert issued. |
|  |  | Post contingency loading on the San Angelo Concho-San Angelo Lake Nasworthy 69 kV line. |
|  | 15:45-22:00 | Transmission Alert issued. |
|  |  | Post contingency loading on the Live Oak - El Dorado 69 kV line. |
|  | 15:45-22:00 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek 345/138 kV Tr. 2 loads San Angelo Red Creek 345/138 kV Tr. 1 |
| 7/15 | 13:15-23:45 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
|  | 15:15-23:00 | Transmission Alert issued. |
|  |  | Loss of Gibbons Creek - Greens Prarie loads Gibbons Creek - East 138 kV. |
|  | 15:15-23:00 | Transmission Alert issued. |
|  |  | Post contingency loading on the Live Oak - El Dorado 69 kV line. |
|  | 15:15-23:00 | Transmission Alert issued. |
|  |  | Post contingency loading on the San Angelo Concho-San Angelo Lake Nasworthy 69 kV line. |
|  | 15:15-23:00 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek 345/138 kV Tr. 2 loads San Angelo Red Creek 345/138 kV Tr. 1 |
| 7/16 | 11:30-24:00 | Transmission Alert issued. |
|  |  | Post contingency loading in the Laredo Area |
|  | 16:00-21:15 | Transmission Alert issued. |
|  |  | Post contingency loading on the San Angelo Concho-San Angelo Lake Nasworthy 69 kV line. |
| 7/17 | 13:30-23:30 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
| 7/19 | 12:00-24:00 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
|  | 14:05-24:00 | Transmission Alert issued. |
|  |  | Post contingency loading in the San Angelo Area. |
|  | 15:10-24:00 | Transmission Alert issued. |
|  |  | Loading on Sandow Transformer |
|  | 16:00-19:00 | Transmission Emergency declared |
|  |  | Loading on Sandow Transformer and local 138 kV lines |
| 7/20 | 11:15-24:00 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
|  | 14:00-24:00 | Transmission Alert issued. |
|  |  | Loss of Dilley - San Miguel loads Pleasanton - Jourdanton 69 kV. |
|  | 15:00-24:00 | Transmission Alert issued. |
|  |  | Post contingency loading in the San Angelo Area. |
|  | 15:00-24:00 | Transmission Alert issued. |
|  |  | Loss of Lon Hill 138/69 kV Tr 2 loads Lon Hill 138/69 kV Tr 1 |
| 7/21 | 11:45-23:00 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
|  | 13:30-23:00 | Transmission Alert issued. |
|  |  | Loss of Dilley - San Miguel loads Pleasanton - Jourdanton 69 kV. |
|  | 14:00-23:00 | Transmission Alert issued. |
|  |  | Post contingency loading in the San Angelo Area. |
|  | 16:00-23:00 | Transmission Alert issued. |
|  |  | Loss of Uvalde - Hamilton loads Asherton - West Conaco |
|  | 12:30-23:00 | Transmission Alert issued. |
|  |  | Loss of Uvalde - Hamilton loads Asherton - West Conaco |
|  | 12:30-23:00 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
| 7/22 | 15:15:23:00 | Transmission Alert issued. |
|  |  | Loss of Dilley - San Miguel loads Pleasanton - Jourdanton 69 kV. |
|  | 15:15:23:00 | Transmission Alert issued. |
|  |  | Post contingency loading in the San Angelo Area. |
| 7/23 | 14:30-24:00 | Transmission Alert issued. |
|  |  | Loss of San Angelo Red Creek - San Angelo North loads San Angelo Concho 138/69 kV Tr. |
|  | 14:30-24:00 | Transmission Alert issued. |
|  |  | Post contingency loading in the San Angelo Area. |
| 7/25 | 14:50-23:15 | Transmission Alert issued. |
|  |  | Post contingency loading in the San Angelo Area. |
| 7/28 | 12:00-24:00 | Transmission Alert issued. |
|  |  | Post contingency loading in the San Angelo Area. |
|  | 15:13-18:53 | Transmission Alert issued. |
|  |  | Loss of Dilley - San Miguel loads Pleasanton - Jourdanton 69 kV. |
|  | 15:30-16:15 | Transmission Alert issued. |
|  |  | Loss of Cagnon - Marbach loads Bandera - Medical Center |
|  | 16:00-16:15 | Transmission Alert issued. |
|  |  | Loss of Lake Creek - Jewett loads Navarro - Richland Chambers |
| 7/29 | 11:10-23:00 | Transmission Alert issued. |
|  |  | Post contingency loading in the San Angelo Area. |
|  | 14:30-21:00 | Transmission Alert issued. |
|  |  | Loss of Dilley - San Miguel loads Pleasanton - Jourdanton 69 kV. |
| 7/30 | 14:15-23:30 | Transmission Alert issued. |
|  |  | Post contingency loading in the San Angelo Area. |
| 7/31 | 13:00-24:00 | Transmission Alert issued. |
|  |  | Post contingency loading in the San Angelo Area. |

# Communication

7/10  Held 14:45 interval.  Incorrect Constraint Limit entered in the MOI.

7/23  POS system not available during intervals below.  Deployed regulation froze at current levels.

12:14 – 12:35

15:08 – 15:17

16:52 – 17:03

17:15 – 17:56

Major Computer Problems & Fixes

7/19  	POS system unavailable from 01:22 until 01:55.  Frequency control and Short-Term Load

Forecast were unavailable during this time contributing to a high frequency event at 02:20

7/21 10:37- 7/23 17:54	  POS system unavailable intermittently causing ERCOT to lose frequency    control and system monitoring.  A larger set of dynamic limits exceeded the capability of the SCADA system causing it to freeze.  The new dynamic limit set has been removed from production.

ERCOT peak (Unofficial)

7/15  17:00  56,500

## Max Temperature

7/2	105   Far West