## Slide 1
ERCOT COMPLIANCE
Aug. 10, 2004
Mark Henry, ERCOT Compliance

## Slide 2: 2004 UFLS Survey
2 companies short in survey have submitted plans to correct problem this fall
Compliance will track completion

## Slide 3: NERC Blackout Update
NERC’s Planning Committee requested disturbance recorder information by August 31. Compliance will work with SPWG
Rev. 0 standards – first round of comments were due yesterday; NERC functional model assignments are an issue.

## Slide 4: Revision to Investigation Process
Initial reports sent within 1 hour to ERCOT Operations, who will forward to NERC
Review frequency events that should trip emergency UFLS, not Laar
Additional event types as developed by NERC may need to be reported within 1 hour
Followup reports from TO’s should be sent to ERCOT

## Slide 5: Minor Events Under Investigation
2 instances of three simultaneous unit trips in June; appear to be related to directly connected transmission events.
Gas supply curtailments threatened due to OOME in July
345kV transmission event with bus failing to clear on breaker failure, remote clearing activated
Firm load shed for transmission security

## Slide 6: Frequency, Ramp SCE Reporting
ROS requested tracking of all QSE’s Schedule Control Error in the periods immediately before and after 0600 and 2200
Method does not account for error as a percentage of total obligation (which is confidential)
Draft PRR525 offers alternative