## Slide 1: Discussion of Curtailment Threshold Criteria for Generation Redeployment to Manage Local Congestion
August 10, 2004

## Slide 2: Operating Review Group Meeting – August 9, 2004
At the request of the QSE Managers, an ERCOT Operations Review Group meeting was held on August 9th to address the following questions and requests:
  What Curtailment Threshold is being used by ERCOT today when managing Local Congestion (e.g. how low can the generation shift factor {GSF} of a particular unit be on a constraint before it is omitted for congestion management)?
  Review the specific costs for managing the post contingency overload of Jewett – Watson Chapel 138 kV Line for the loss of the Gibbons Creek – Twin Oak double circuit 345 kV Line on July 7th and 12th
  Discuss the work being done by ERCOT Operations, Brazos, & TXU Electric Delivery to develop a RAP to manage the binding constraint described above.
  Begin discussion around which, if any, policy changes would be necessary to minimize the amount of low GSF impact Local Congestion deployments to manage binding constraints where no online units have significant impact.
  Review the specific obstacles that often prevent ERCOT from being able to utilize all of the apparently available resources for Local Congestion management.

## Slide 3: Triggering Event Background
On the afternoon of July 7, 2004, TXU QSE received unit specific Local Balancing instructions to back down the following generating units as a part of ERCOT Operations local congestion management for the post contingency overload of Jewett – Watson Chapel 138 kV Line for the loss of the Gibbons Creek – Twin Oak double circuit 345 kV Line:
  Approx. 1,100 MW of Martin Lake generation (lignite/coal)
  Approx. 225 MW of TNP One (lignite/coal)
  Approx. 300+ MW of Stryker (gas)
TXU Portfolio Management’s analysis of this binding constraint indicates that no generator has more than a 2.9% generation shift factor impact for loading up the subject line and not very many units have the capability to unload it.

## Slide 4: Further Background On This Specific Binding Constraint
At the August 9th Operations Review Group meeting, ERCOT Staff indicated that:
  For the 15 interval (3 hour & 45 minute) period while the constraint occurred on July 7th,
    ERCOT issued on average 1,777 MW (min of 1,288 – max of 2,340) of unit specific balancing instructions (average generation shift factor impact of 2.2%).
    Preliminary cost estimate of $189,000.
  For the 33 interval (8 hour & 15 minute) period while the constraint occurred on July 12th,
    ERCOT issued on average 1,167 MW (min of 55 – max of 3,024) of unit specific balancing instructions.
    Preliminary cost estimate of $272,000.
During the period from June 1, 2004 through August 8, 2004 (69 day period) this binding constraint has occurred on 27 days (i.e. 40% of the days).

## Slide 5: Illustration of the GSF Impact of the Generation on the Constraint
Bottom Line – the constraint is primarily a load serving problem, not a generation export problem.
Only three units in the Bryan area have any meaningful impact on this constraint. They may be off-line if not OOMC’d day-ahead.
The low GSFs of these units on the constraint, indicate that they don’t meaningfully contribute to the problem.

## Slide 6: Major Shift Factor Impacts
Most Significant Loading Contribution
  2.9% - Stryker (675 MW) & TNP One (308 MW)
  2.8% - Limestone (1,532 MW)
  2.7% - Champion Paper (42 MW)
  2.6% - Trinidad (240 MW)
  2.5% - Big Brown (1,162 MW), Freestone County (1,134 MW), Gateway (954 MW), Martin Lake (2,285 MW)
  2.3% - Forney (1,775 MW)
Most Significant Unloading Contribution
  -14.2% - Texas A&M Gen (32 MW)
  -14.0% - Dansby (114 MW)
  -13.0% - Atkins (129 MW)
  -4.7% - Gibbons Creek (462 MW)
  -4.1% - Frontier (830 MW)

## Slide 7: Reasons that a resource might not be deployed for Local Cong. Mgmt
ERCOT Operations identified six primary reasons that a resource might not actually be used for Local Congestion management:
  Resource plan shows offline and/or unavailable
  System will not move unit below min MW or above max MW provided by QSE in Resource Plan
  QSE has limited or no BES bids for that zone
  QSE has very small portfolio ramp rate
  QSE’s energy schedules are not accommodated by Resource Plan values, leading SPD to estimate incorrect output levels
  Resource current output significantly deviated from its resource plan

## Slide 8: Meeting Highlights & Wrap Up
ERCOT Operations stated that they were currently using a Curtailment Threshold of 2%
ERCOT Operations reported that they and Brazos were actively working to develop and implement a viable Remedial Action Plan to eliminate the continued need to utilize Local Congestion management for this constraint. An email will be sent out within one week to update group on the progress of implementing this RAP, as well as, potential long-term transmission upgrade options.
ERCOT Operations committed to provide an estimate of the money spent to manage the Jewett – Watson Chapel 138 kV post contingency overload during the period of review within the next week.
ERCOT Operations identified the six primary reasons that a resource might not be deployed for Local Congestion management.
Discussion occurred around the cost of maintaining reliability with the current Curtailment Threshold set as low as 2%.
  No proposed solutions were agreed upon at the meeting.
  More thought needs to be given to the issue and options reviewed on their merit.
ERCOT Operations encouraged stakeholders who had further thoughts or concerns about the Curtailment Threshold issue to bring them forward for consideration.
It was established that there is some settlement intervals where Local Congestion management instructions are significantly depleting the zonal bid stacks causing MCPE price irregularities.