## Slide 1: 2005 – Methodologies for Determining AS Requirements
J. Adams

## Slide 2: Quick Review – 2004 Methods
Regulation – mean of historic usage
Responsive reserve – 2300 MW
Non-spin – flow chart – if expected temperature > 95 or < 30 purchase Nonspin equal to largest unit. Etc.(+ Other conditions)

## Slide 3: Quick Review – 2004 Methods
Replacement reserve – calculate sum of requirements –minus resource plan available. If insufficient procure more.
Minimum balancing down requirement - average amount of frequency deviation during periods of high frequency will be analyzed for the season.

## Slide 4: 2005 Recommended Changes
Regulation – Old: re-evaluate monthly by 20th of month. Look at current & equivalent month 1 year ago. Calculate mean and standard deviation of deployments. Select amount to cover 2.5 standard deviations. (98.8% of time will not exhaust regulation)
New: Analyze 0600 & 2200 for ramp rate required. Add this additional ramp rate requirement to need.

## Slide 5: 2005 Recommended Changes
Responsive reserve requirement – no change (2300 MW)
Non-spin reserve – no change (>92° etc)
Replacement reserve – New replacement program

## Slide 6: Review Regulation Calculation
U = 60.85, Std dev = 372.32

## Slide 8: Interim Result – Hourly requirement

## Slide 9: Grouping & Rounding

## Slide 10: UREG & DREG Requirement EXAMPLE

## Slide 11: 2005 - In addition to the previous
Hour 0600 – Examine each period around 0600 of month for delta frequency over minutes. Convert this frequency error to a MW ramping requirement by multiplying times bias. Add this to the 0600 -0700 requirements.
Hour 2200: Same for 2200-2300.