## 2004 Fleet Deployments
2004 Fleet Deployments
Deployments
| Zonal |  | ERCOT-Wide
Trade Date | UP | Down | UP | Down | Zone | QSE Name | Energy, MWh | Reasons for Fleet Deployment
2004-01-08 |  |  |  | 125 |  | Texas Genco | 119.7 | Out of reg down & Freq holding at 60.05
2004-01-09 |  |  | 75 |  |  | TXU | 54 | Out of UP Reg
2004-01-09 |  |  | 112.5 |  |  | Texas Genco | 94.6 | Out of UP Reg
2004-01-12 |  |  |  | 100 |  | Texas Genco | 100 | Out of reg down & Freq holding at 60.04
2004-01-16 |  |  | 75 |  |  | Texas Genco | 46.3 | Freq at 59.94 & 45MW of reg available
2004-02-12 |  |  | 100 |  |  | TXU | 100 | Out of reg, ACE at 350MW & Freq at 59.91
2004-03-03 |  |  | 225 |  |  | TXU | 86.5 | Freq at 60.06 & no Down reg
2004-03-05 |  | 100 |  |  | N04 | TXU | 0 | No Down reg
2004-03-28 |  |  | 150 |  |  | TXU | 61.1 | Freq at 59.91 & No Up reg
2004-03-28 |  |  | 50 |  |  | LCRA | 42.9 | Freq @ 59.93 & No Up reg
2004-03-28 |  |  | 202.5 |  |  | AEP | 21.9 | Freq @ 59.91 & no Up reg
2004-03-29 |  |  | 100 |  |  | TXU | 99.42 | Bad STLF Number entered in study
2004-03-30 |  |  | 200 |  |  | TXU | 167.34 | Freq @ 59.97 & 100MW of Up reg available
2004-04-26 |  |  | 400 |  |  | Texas Genco | 322.3 | ACE at 7000MW, Freq 59.86
2004-05-13 |  |  | 100 |  |  | TXU | 76.2 | Freq below 59.95, system not keeping up with Load Pickup
2004-05-26 |  |  | 250 |  |  | Texas Genco | 171.97 | Bad offset due to Load Forescast
2004-05-26 |  |  | 625 |  |  | TXU | 588.25 | Bad offset due to Load Forescast
2004-05-31 |  |  | 200 |  |  | Texas Genco | 200 | ACE at 545 and out of UP regulation
2004-06-01 | 16.5 |  |  |  | H04 | Dynegy | 16.45 | MOI down, N-Houston Flow
2004-06-01 |  |  |  | 100 |  | TXU | 100 | Out of reg down & Freq holding at 60.05 - 60.07, Load Pickup I slow
2004-06-01 |  |  |  | 100 |  | Texas Genco | 100 | Out of reg down & Freq holding at 60.05 - 60.07
2004-06-01 |  |  |  | 75 |  | Texas Genco | 75 | Freq at 60.122 and not dropping
2004-06-01 |  |  |  | 800 |  | Texas Genco | 800 | Freq at 60.122 and not dropping
2004-06-01 |  |  |  | 1000 |  | TXU | 721.54 | Freq at 60.188
2004-06-02 |  |  |  | 200 |  | Texas Genco | 200 | Out of reg down. Freq at 60.92
2004-06-09 |  |  | 25 |  |  | TXU | 25 | Out of reg down. Freq at 59.938
2004-06-23 |  |  |  | 175 |  | TXU | 175 | Computer problems, no reg down
2004-06-23 |  |  |  | 437.91 |  | Texas Genco | 426.67 | Computer problems, no reg down
2004-07-05 |  |  | 225 |  |  | TXU | 225 | Low freq, reg up depleted
| 16.5 | 100 | 3115 | 3112.91 |  |  | 5217.14

## 2003 Fleet Deployments
2003 Fleet Deployments
Deployments
| Zonal |  | ERCOT-Wide
Trade Date | UP | Down | UP | Down | Zone | QSE Name | Energy, MWh | Reasons for Fleet Deployment
2003-05-05 | 4150 |  |  |  | H03 | TX GENCO | 3360.5 | Houston Import
2003-05-06 |  | 50 |  |  | H03 | TX GENCO | 50 | Frequency at 61.1
2003-05-06 |  | 50 |  |  | N03 | TXU | 0 | Frequency at 61.1
2003-05-08 | 1125 |  |  |  | H03 | TX GENCO | 984 | Houston Import
2003-05-08 | 150 |  |  |  | N03 | TXU | 150 | Out of Regulation and ACE at -365. Freq at 59.94
2003-05-12 | 9487.5 |  |  |  | H03 | TX GENCO | 9215.7 | Houston Import
2003-05-12 |  | 525 |  |  | N03 | TXU | 398.3 | Frequency at 60.09 and ACE at 525MW
2003-05-13 |  | 150 |  |  | S03 | LCRA | 107.9 | ACE at 453 MW and Frequency at 60.077
2003-05-13 | 13625 |  |  |  | H03 | TX GENCO | 12393.8 | Houston Import
2003-05-14 |  | 75 |  |  | H03 | TX GENCO | 75 | Regulation Down at 0 and Freq. at 60.058
2003-05-14 | 225 |  |  |  | N03 | TXU | 225 | Regulation UP at 120. Freq. at 59.92 and ACE at -471
2003-05-15 | 135 |  |  |  | S03 | AEP | 20.7 | Units tripped in the system and Freq. fell to 59.28, EMS failed
2003-05-15 | 150 |  |  |  | S03 | LCRA | 35.4 | Units tripped in the system and Freq. fell to 59.28, EMS failed
2003-05-15 | 255 |  |  |  | H03 | TX GENCO | 178.3 | Units tripped in the system and Freq. fell to 59.28, EMS failed
2003-05-18 | 562.5 |  |  |  | H03 | TX GENCO | 117 | North - Houston Import
2003-05-18 |  | 562.5 |  |  | N03 | TXU | 27.6 | North - Houston Import
2003-05-19 | 500 |  |  |  | H03 | TX GENCO | 109.1 | North - Houston Import
2003-05-19 |  | 500 |  |  | N03 | TXU | 0 | North - Houston Import
2003-05-20 | 16525 |  |  |  | H03 | TX GENCO | 13909.5 | North - Houston Import
2003-05-20 |  | 16525 |  |  | N03 | TXU | 7123.8 | North - Houston Import
2003-05-21 | 20325 |  |  |  | H03 | TX GENCO | 16133 | North - Houston Import
2003-05-21 |  | 20325 |  |  | N03 | TXU | 12393 | North - Houston Import
2003-05-21 | 200 |  |  |  | N03 | TXU | 200 | Freq not responding at 59.92/no up regulation
2003-05-24 | 1000 |  |  |  | H03 | CALPINE | 102.1 | No generation in Houston
2003-05-24 |  | 800 |  |  | N03 | CALPINE | 0 | No generation in Houston
2003-05-24 | 2575 |  |  |  | H03 | TX GENCO | 2410.4 | No generation in Houston
2003-05-24 |  | 2575 |  |  | N03 | TXU | 446.5 | No generation in Houston
2003-05-25 | 1425 |  |  |  | H03 | TX GENCO | 844.9 | No generation in Houston
2003-05-25 |  | 1675 |  |  | N03 | TXU | 212.7 | No generation in Houston
2003-05-26 | 4075 |  |  |  | H03 | TX GENCO | 3275.3 | Houston Import
2003-05-26 |  | 4075 |  |  | N03 | TXU | 1230.8 | Houston Import
2003-05-28 | 2250 |  |  |  | H03 | TX GENCO | 1311 | Out of Regulation and Frequency issues
2003-05-28 |  | 1550 |  |  | N03 | TXU | 776.3 | Out of Regulation and Frequency issues
2003-05-28 | 500 |  |  |  | N03 | TXU | 500 | Out of Regulation and Frequency issues
2003-06-01 | 225 |  |  |  | H03 | TX GENCO | 225 | Frequency Low
2003-06-02 | 1425 |  |  |  | H03 | TX GENCO | 1350.1 | Hi Freq/No Regulation
2003-06-02 |  | 300 |  |  | H03 | TX GENCO | 300 | Hi Freq/No Regulation
2003-06-02 |  | 2025 |  |  | N03 | TXU | 541.8 | Out of Reg Down
2003-06-03 | 675 |  |  |  | H03 | TX GENCO | 675
2003-06-03 |  | 675 |  |  | N03 | TXU | 0 | No generation in Houston
2003-06-05 | 100 |  |  |  | H03 | CALPINE | 27 | ERCOT SCADA Problems
2003-06-05 | 600 |  |  |  | H03 | TX GENCO | 530.2 | North to Houston Load Control
2003-06-05 |  | 600 |  |  | N03 | TXU | 570.4 | North to Houston Load Control
2003-06-06 | 10325 |  |  |  | H03 | TX GENCO | 6000.5 | North to Houston Constraint
2003-06-06 |  | 7925 |  |  | N03 | TXU | 2718.8 | North to Houston Constraint
2003-06-08 |  |  | 200 |  |  | TX GENCO | 59.4 | Freq at 59.91 and out of Regulation
2003-06-08 |  |  |  | 225 |  | TXU | 67.7 | Out of Down Reg, and Freq at 60.05
2003-06-12 | 3840 |  |  |  | H03 | TX GENCO | 2905.8 | Area Security
2003-06-12 |  | 9150 |  |  | N03 | TXU | 4732.5 | Area Security
2003-06-13 | 995 |  |  |  | H03 | TX GENCO | 290 | Area Security
2003-06-13 |  | 7387.5 |  |  | N03 | TXU | 2735.2 | North - Temple; out of reg down
2003-06-16 |  |  | 250 |  |  | TX GENCO | 133.4 | Out of Regulation up and frequency at 59.945
2003-06-17 |  |  | 437.5 |  |  | LCRA | 424.1 | Out of reg, TXU and TXGENCO can't move due to VDI and OOM
2003-06-17 | 1300 |  |  |  | H03 | TX GENCO | 1267.6 | Houston Import
2003-06-18 |  |  | 150 |  | S03 | LCRA | 77 | Out of reg up and Freq. at 59.94
2003-06-18 |  |  | 300 |  | H03 | TX GENCO | 33.2 | Out of reg up and Freq. at 59.954
2003-06-18 |  |  |  | 250 |  | TXU | 68.55 | Out of reg dp and Freq. at 60.85
2003-06-18 |  |  | 50 |  |  | TXU | 33.6 | Out of reg up and Freq. at 59.95
2003-07-02 |  |  |  | 300 |  | CALPINE | 255.5 | Out of down reg due to BE being held
2003-07-02 |  |  |  | 375 |  | TXU | 375 | Out of down reg due to BE being held
2003-07-06 | 1825 |  |  |  | H03 | TX GENCO | 967.9 | North to Houston Import
2003-07-12 | 100 |  |  |  | N03 | TXU | 100 | Out of Reg Up and Holding below 60.00
2003-07-13 | 500 |  |  |  | H03 | TX GENCO | 374.8 | Out of regulation up and frequency at 59.93
2003-07-29 |  |  |  | 625 |  | TXU | 549.2 | MOS not Functioning
2003-08-03 | 1725 |  |  |  | H03 | TX GENCO | 1371.4 | North to Houston
2003-08-03 |  | 1725 |  |  | N03 | TXU | 1621 | North to Houston
2003-08-08 | 1725 |  |  |  | H03 | TX GENCO | 1351.1 | North to Houston; Out of regulation and frequency at 59.94
2003-08-09 | 4975 |  |  |  | H03 | TX GENCO | 4666.6 | North to Houston
2003-08-09 |  | 2687.5 |  |  | N03 | TXU | 1823.9 | North to Houston
2003-08-11 |  |  |  | 250 |  | TX GENCO | 250 | Frequncy at 60.11
2003-08-15 |  |  |  | 300 |  | TX GENCO | 272.2 | Frequncy at 60.060 and out of regulation
2003-08-16 |  |  | 75 |  |  | CALPINE | 75 | Out of regulation and frequency at 59.91
2003-08-16 |  |  | 100 |  |  | TX GENCO | 100 | Out of regulation and frequency at 59.94
2003-08-16 |  |  | 300 |  |  | TXU | 198.7 | Out of regulation and frequency at 59.91
2003-08-18 | 2500 |  |  |  | H03 | TX GENCO | 1136.6 | North to Houston Import
2003-08-18 |  | 1200 |  |  | N03 | TXU | 133.9 | North to Houston Import
2003-08-19 | 3500 |  |  |  | H03 | TX GENCO | 2517 | North to Houston Import
2003-08-19 |  | 3100 |  |  | N03 | TXU | 1948.7 | North to Houston Import
2003-08-26 | 3250 |  |  |  | H03 | TX GENCO | 1571.3 | North to Houston Limit
2003-08-26 |  | 1875 |  |  | N03 | TXU | 469.7 | North to Houston Limit
2003-08-27 | 5750 |  |  |  | H03 | TX GENCO | 3696.9 | North to Houston Congestion
2003-08-27 |  | 5750 |  |  | N03 | TXU | 2579.3 | North to Houston Congestion
2003-08-28 | 500 |  |  |  | H03 | TX GENCO | 301.4 | Out of Reg Up, Freq Low
2003-09-01 |  | 2400 |  |  | N03 | TXU | 564.2 | North to Houston Congestion
2003-09-02 |  | 900 |  |  | N03 | TXU | 147.1 | North to Houston Congestion
2003-09-03 |  | 1350 |  |  | N03 | TXU | 28.6 | North to Houston
2003-09-05 | 750 |  |  |  | H03 | TX GENCO | 0 | North to Houston Import
2003-09-08 |  |  | 625 |  |  | TX GENCO | 538.5 | Out of Regulation, Frequency at 59.90
2003-09-08 |  |  | 500 |  |  | TXU | 500 | Out of Regulation, Frequency at 59.93
2003-09-09 |  |  | 225 |  |  | TX GENCO | 205.5 | Out of UP Regulation, Frequency at 59.92
2003-09-10 | 500 |  |  |  | H03 | TX GENCO | 487.2 | Transmission Outage
2003-09-10 |  | 2500 |  |  | N03 | TXU | 397.4 | Transmission Outage
2003-09-12 | 1050 |  |  |  | H03 | TX GENCO | 949.8 | North to Houston Import
2003-09-14 | 2550 |  |  |  | H03 | TX GENCO | 2228.7 | North to Houston Import
2003-09-14 |  | 2325 |  |  | N03 | TXU | 1068.6 | North to Houston Import
2003-09-14 | 300 |  |  |  | N03 | TXU | 300 | Out of UP Regulation, Low Frequency
2003-09-15 | 100 |  |  |  | H03 | TX GENCO | 23.9 | Out of Up Regulation. Low Frequency
2003-09-15 |  | 1650 |  |  | N03 | TXU | 0 | North to Houston Import
2003-09-15 | 300 |  |  |  | N03 | TXU | 201.1 | Out of Up Regulation. Low Frequency
2003-09-25 |  |  |  | 75 |  | TX GENCO | 15.6 | High Frequency, REG not Deployed Fast Enough
2003-10-04 |  |  |  | 625 |  | CALPINE | 602.2 | TXGenco had 1479 MW Mismatch Sched
2003-10-04 |  |  |  | 500 |  | TX GENCO | 0 | TXGenco had 1479 MW Mismatch Sched
2003-10-17 |  | 150 |  |  | H03 | TX GENCO | 21 | EMS has failed
2003-10-20 |  | 175 |  |  | H03 | TX GENCO | 175 | Frequency at 60.07 and out of Down regulation
2003-10-21 |  | 225 |  |  | H03 | TX GENCO | 141.7 | Frequency at 60.092 and out of Down regulation
2003-10-21 |  | 100 |  |  | N03 | TXU | 61.7 | Frequency at 60.092 and out of Down regulation
2003-10-25 | 325 |  |  |  | H03 | TX GENCO | 139.1 | Frequency at 59.94 and out of Up regulation, ACE at -265MW
2003-10-25 | 75 |  |  |  | N03 | TXU | 0 | Frequency at 59.94 and out of Up regulation, ACE at -265MW
2003-11-03 |  |  | 100 |  |  | TX GENCO | 39.5 | Lighting Load Picked Up Sooner than Expected
2003-11-11 | 150 |  |  |  | S03 | LCRA | 67.4 | Frequency at 59.878 and not responding
2003-11-21 | 100 |  |  |  | S03 | LCRA | 27.8 | ACE at 400 MW and Frequency at 59.926
2003-11-21 |  |  | 125 |  |  | TXU | 123.1 | ACE at 501 MW and Frequency at 59.906
2003-11-24 |  |  | 200 |  |  | TXU | 195.2 | Out of regulation, and frequency at 59.91
2003-11-28 |  |  | 225 |  |  | TXU | 224.9 | 0 regulation and frequency was not crossing zero
2003-12-03 |  |  | 250 |  |  | TX GENCO | 0 | Comp. Problems at Texas Genco & Lost his BE
2003-12-08 |  | 100 |  |  | N03 | TXU | 100 | Reg Down Depleted, High Frequency
2003-12-09 |  |  |  | 75 |  | TX GENCO | 75 | Reg Down Depleted, High Frequency
2003-12-12 |  |  |  | 300 |  | TX GENCO | 170.3 | High Frequency (60.112 HZ)
2003-12-22 |  |  |  | 150 |  | TX GENCO | 46.6 | High Frequency (60.137 HZ) and not responding
2003-12-29 |  |  |  | 225 |  | TXU | 130.2 | Out of Regulation and Frequency at 60.08
| 131275 | 105712.5 | 4112.5 | 4275 |  |  | 152788.45

## 2004 Plant Deployments
2004 PLANT INSTRUCTIONS
Trade Date | Zone | PLANT NAME | DIRECTION | Deployed MWh | QSE Name | Paid Energy, MWh | Deployment Reasons
1-8-04 | E04 | KMCHI | DOWN | 9300 | Coral | 9300 | ??????-Cnses outage - Coral DBES deployments were such that they would pick up Kiamichi generation to meet their deployments
3-15-04 | E04 | LPCCS | DOWN | 325 | FPL | 323.75 | Constraints - trans outage Paris switch - Valley Switch 345kv
3-15-04 | E04 | LPCCS | DOWN | 1087.5 | FPL | 1073 | Paris Switch - Valley Switch 345kv
3-22-04 | S04 | OXYGEN | UP | 949.75 | TENASKA | 0 | Reliability
3-29-04 | W04 | OKLA_OKLA | DOWN | 27.5 | AEP | 11.38 | 6558 @ Wfalls
3-29-04 | W04 | OKLA_OKLA | DOWN | 297.5 | AEP | 98.94 | 6558 @ Wfalls
4-1-04 | S04 | FRONTERA_FRONTEG | UP | 393.75 | FRONTERA | 374.39 | Leon Creek - Pleasanton Post Cont.
4-6-04 | S04 | FRONTERA_FRONTEG | DOWN | 315 | FRONTERA | 306.86 | Relieve Congestion Bates/Garza
4-7-04 | S04 | RIONOG | DOWN | 843.75 | CONSTELLATION | 679.71 | Vendor Testing
4-13-04 | N04 | FRNYPP | DOWN | 1190 | FPL | 1175.3 | 40 BB-Venus 345kv on 3040A Watermille at 106.1%
4-19-04 | S04 | CCEC | UP | 345 | CAPLPINE | 344.8 | I sent the wrong amounts
4-19-04 | W04 | OKLA_OKLA | DOWN | 322 | AEP | 281 | Outage on Bowman circuit breaker CB6030
5-18-04 | W04 | OECCS | DOWN | 555 | BPTX | 529 | 6500_B
5-19-04 | W04 | OECCS | DOWN | 3330 | BPTX | 3244.5
5-24-04 | W04 | OECCS | DOWN | 591.5 | BPTX | 547 | Midland East Odessa. SMDLODES Constraint
5-26-04 | N04 | FRNYPP | DOWN | 1625 | FPL | 1609.8 | Post contingency loss of West-levee Sw T-1 overloading line 313 Industry compton
5-31-04 | S04 | GUADG | DOWN | 675 | BPTX | 632.5
6-1-04 | H04 | PSG_PSG | UP | 150 | CALPINE | 96.918 | Mo 1 down North-Houston
6-2-04 | E04 | KMCHI | DOWN | 6420.5 | CORAL | 6369.9937 | Due to system security issues.
6-2-04 | N04 | TGCCS | DOWN | 2864 | CORAL | 2814 | Due to system security issues.
6-2-04 | S04 | GUADG | DOWN | 565 | BPTX | 552 |  | ?
|  |  |  | 32172.75 |  | 30364.8417
* This is the absolute value of RP minus VDI.