| OGRR Number | 155OGRR | OGRR Title | Section 3 Corrections and Clarifications |
| --- | --- | --- | --- |
| Operating Guide Section Requiring Revision |  | Section 3, Operational Interfaces |  |
| Protocol Section Requiring Revision, if any. |  | ## None |  |
| Requested Resolution |  | ## Normal |  |
| Revision Description |  | Implements Protocol and Operating Guides Reference Corrections, Section title corrections, punctuation corrections, corrections to pre deregulation language, and defined term corrections. Removes redundant and unnecessary language. |  |
| ###### Reason for Revision |  | Eliminate inaccuracies and inconsistencies. |  |
| Timeline |  |  |  |
| Date Posted |  | 8/27/04 |  |
| Please see the Master List on the ERCOT website for current timeline information. |  |  |  |

| Sponsor |  |
| --- | --- |
| Name | David A. Darnell on behalf of OGRTF |
| E-mail Address | dadarnell@cps-ems.com |
| Company | City Public Service |
| Company Address | P.O. Box 1771, San Antonio, TX 78296 |
| Phone Number | 210 353 2208 |
| Fax Number | 210 353 3340 |

Proposed Operating Guide Language Revision

Section 3:  Operational Responsibilities and Testing Requirements

QSE, PGC, and TDSP Interaction with ERCOT

June 1, 2004

Contents

3.	Operational Responsibilities and Testing Requirements	2

3.1	System Control Interfaces with ERCOT	2

3.1.1	Introduction	2

3.1.2	Compliance with Dispatch Instructions	2

3.1.3	Qualified Scheduling Entities	2

3.1.3.1	Operating Obligations	2

3.1.3.2	Daily Resource Plan	2

3.1.3.3	Unplanned Load Changes	2

3.1.3.4	QSE Responsibility for Department of Energy (DOE) and NERC Reportable Events	2

3.1.4	Power Generation Companies	2

3.1.4.1	Federally Licensed PGCs	2

3.1.4.2	PGC Data Reporting	2

3.1.4.3	Unit Capability Testing Requirement	2

3.1.4.4	Unit Reactive Capability Testing and AVR Testing	2

3.1.4.5	Turbine Governor Speed Testing	2

3.1.4.6	Enforcement of Testing Requirements	2

3.1.4.7	Automatic Voltage Regulators And Power System Stabilizers	2

3.1.4.8	Protective Relaying Requirement	2

3.1.4.9	Outages	2

3.1.4.10	Enforcement of Load acting as a Resource (LaaR) Testing Requirement	2

3.1.5	Transmission and/or Distribution Service Providers	2

3.1.5.1	Transmission Operator Responsibility for Department of Energy (DOE) and NERC Reportable Events	2

3.1.5.2	Outages	2

3.1.6	Responsibility For Equipment Ratings	2

3.2	Scheduling Interfaces with ERCOT	2

3.2.1	Reserved	2

3.2.2	Scheduling Process	2

3.2.2.1	Day Ahead Scheduling	2

3.2.2.2	Adjustment Period Scheduling	2

3.2.3	Procurement of Replacement Reserve Service Resources	2

3.2.4	Procurement of Additional Ancillary Services	2

3.3	Document Control	2

Protocol References

Reference:  Protocols, Section 5.4.4, Compliance with Dispatch Instructions	2

Reference:  Protocols, Section 4.3.4, Operations of the Qualified Scheduling Entity	2

Reference:  Protocols, Section 4.4.15, QSE Resource Plans	2

Reference:  Protocols, Section 5.5.1, Changes in Resource Status	2

Reference:  Protocols, Section 6.10.2, General Capacity Testing Requirements	2

Reference:  Protocols, Section 6.10.3.5, Reactive Supply from Generation Resources required to provide VSS	2

Reference:  Protocols, Section 5.5.2, Changes in Transmission Facility Status	2

Reference:  Protocols, Section 6.4.2, Determination of ERCOT Control Area Requirements	2

Reference:  Protocols, Section 4.3.2, Schedule Components	2

Reference:  Protocols, Section 4.3.3, Special Scheduling Considerations for Split Generation Meters	2

Reference:  Protocols, Section 4.3.5, Requirement for Balanced Schedules	2

Reference:  Protocols, Section 4.1.1, Day Ahead Scheduling Process, and Operating Guides Section 2.5.1	2

Reference:  Protocols, Section 4.1.2, Adjustment Period Scheduling Process	2

Reference:  Protocols, Section 4.4.18.4, Settlement	2

Reference:  Protocols Sections 4.9.1, Dynamic Load Schedules, 4.9.2, Approval of the Use of Dynamic Load Schedules, and 4.9.3, Principles for Dynamic Schedules	2

Reference:  Protocol: Section 4.9.4, Responsibility Transfers (RspT), and 4.9.5, Responsibility Transfer for Balancing Energy Bidding	2

# Operational Responsibilities and Testing Requirements

## 3.1	System Control Interfaces with ERCOT

### 3.1.1	Introduction

ERCOT Control Area Authority is authorized to take specific actions for the purpose of securely operating the ERCOT Transmission Grid in conformance with the standards specified in Section 5.2, North American Electric Reliability Council/ERCOT Tagging Procedures, of the Protocols.

The following sections define the specific interface between Qualified Scheduling Entities and Transmission and/or Distribution Service Providers to allow the Control Area Authority to ensure the security and reliability of the ERCOT System, under normal operations.  Emergency operation is fully described in Section 4: Emergency Operation of this Guide.  PGCs can communicate directly with ERCOT Control Area Authority under emergency and specific scheduling activities.

All other Entities operating in the ERCOT System, interface either to the Qualified Scheduling Entities or the Transmission Operators.

### 3.1.2	Compliance with Dispatch Instructions

Reference:  Protocols, Section 5.4.4, Compliance with Dispatch Instructions

5.4.4	Compliance with Dispatch Instructions

- Each TDSP and each QSE within the ERCOT System shall comply fully and promptly with valid Dispatch Instructions, unless in the sole and reasonable judgment of the TDSP or QSE, such compliance would create a threat to safety, risk of bodily harm or damage to the equipment, or is otherwise not in compliance with these Protocols.

- If the recipient of a valid Dispatch Instruction does not comply because in the sole and reasonable judgment of the TDSP or QSE, such compliance would create a threat to safety, risk of bodily harm or damage to the equipment, or is otherwise not in compliance with these Protocols, then, the TDSP or QSE must immediately notify ERCOT and provide the reason for non-compliance.

- If the recipient of a Dispatch Instruction recognizes that the Dispatch Instruction conflicts with other valid instructions or is invalid, the recipient will immediately notify ERCOT of the conflict and request resolution.

- Upon receipt of Notice of non-compliance or conflict with Dispatch Instructions, ERCOT may, but is not required to, issue new Dispatch Instructions in response to the TDSP or QSE’s Notice.

- ERCOT’s final instruction in effect will apply for all Protocol-related processes.  If the QSE does not comply after receiving the final instruction, the QSE shall remain liable for failure to meet its obligations under the Protocols and shall remain liable for any charges resulting from such failure.

- ERCOT’s final instruction to a TDSP in effect will apply for all Protocol-related processes.  If the TDSP does not comply after receiving the final instruction, the TDSP shall remain liable for such failure under these Protocols in accordance with the TDSP’s Agreement with ERCOT.

- In all cases in which compliance with a Dispatch Instruction is disputed, both ERCOT and the QSE or TDSP shall document their communications, agreements, disagreements, and reasons for their actions, to enable resolution of the dispute through the ADR process in Section 20, Alternative Dispute Resolution.

Each TDSP and each QSE within the ERCOT System shall comply fully and promptly with valid Dispatch Instructions.

The TDSP or QSE shall immediately notify ERCOT if the recipient of a valid Dispatch Instruction does not comply.  The TDSP or QSE shall provide the reason for non-compliance in one of the following categories:

- Threat to safety;

- Risk of bodily harm;

- Damage to the equipment; or

- Not in compliance with the Protocols.

A recipient of a Dispatch Instruction shall immediately notify ERCOT Control Area Authority of any conflicts within acceptable limits and request resolution.  Conflicts within acceptable limits are:

- The Dispatch Instruction conflicts with other valid instructions; or

- The Dispatch Instruction is invalid.

ERCOT Control Area Authority may, but is not required to, alter or retract Dispatch Instructions in response to the TDSP or QSE’s Notice of conflict.

ERCOT Control Area Authority’s final Dispatch Instruction in effect to a QSE shall apply. If the QSE does not comply after receiving the final Dispatch Instruction, the QSE shall remain liable for failure to meet its obligations under the Protocols and shall remain liable for any charges resulting from such failure.

ERCOT Control Area Authority’s final Dispatch Instruction to a TDSP in effect shall apply. If the TDSP does not comply after receiving the final Dispatch Instruction, the TDSP shall remain liable for such failure in accordance with the TDSP’s Agreement with ERCOT.

ERCOT and the QSE or TDSP shall document the following information in the case of a dispute over compliance with a Dispatch Instruction:

- Communications;

- Agreements;

- Disagreements; and

- Reasons for their actions.

Documentation shall be retained for a minimum of three (3) years or until the related dispute is resolved.

Each QSE, or their agent shall immediately forward any valid Dispatch Instruction to the appropriate Resource or group of Resources.

### 3.1.3	Qualified Scheduling Entities

#### 3.1.3.1	Operating Obligations

Reference:  Protocols, Section 4.3.4, Operations of the Qualified Scheduling Entity

4.3.4	Operations of the Qualified Scheduling Entity

Scheduling Center Requirement.  A QSE shall maintain a twenty four (24) hour, seven-day-per-week scheduling center with qualified personnel for the purposes of communicating with ERCOT for scheduling purposes and for deploying the QSE’s Ancillary Services in Real Time.

QSE Representative.  Each QSE shall, for the duration of the Scheduling Process and settlement period for which the QSE has submitted schedules to ERCOT, designate a representative who shall be responsible for operational communications and who shall have sufficient authority to commit and bind the QSE.

A QSE shall maintain a twenty (24) hour, seven-day-per-week scheduling center with qualified personnel for the purposes of communicating with ERCOT for scheduling purposes and for deploying the QSE’s Ancillary Services in Real Time.  Each QSE shall provide the ERCOT Control Area Authority (CAA) with its written backup control plan to continue operation in the event the QSE’s scheduling center becomes inoperable.

Each backup control plan shall be reviewed and updated annually and shall meet the following minimum requirements:

- Description of actions to be taken by QSE personnel to avoid placing a prolonged burden on ERCOT and other Market Participants;

- Description of specific functions and responsibilities to be performed to continue operations from an alternate location;

- Includes procedures and responsibilities for maintaining basic voice communications capabilities with ERCOT; and

- Includes procedures for backup control function testing and the training of personnel.

As an option, the backup plan may include arrangements made with another Entity to provide the minimum backup control functions in the event the QSE’s primary functions are interrupted.

Each QSE shall, for the duration of the Scheduling Process and settlement period for which the QSE has submitted schedules to ERCOT, designate an individual who shall be responsible for operational communications and who shall have sufficient authority to commit and bind the QSE.

A QSE representing a Generation Entity that has Generation Resources connected to a TDSP shall provide the following Real Time data to ERCOT for each individual generating unit at a Generation Resource plant location and ERCOT will make the data available to the Generation Resource’s host TDSP (at TDSP expense):

- Gross or net real power;

- Gross or net Reactive Power;

- If gross quantities are provided, the plant auxiliary Load data will also be supplied;

- Status of switching devices in the plant switchyard not monitored by the TDSP affecting flows on the ERCOT System;

- Frequency Bias of Portfolio Generation Resources under QSE operation;

- Any data mutually agreed by ERCOT and the QSE to adequately manage system reliability;

- Generator breaker status;

- High Operating Limit; and

- Low Operating Limit.

Any QSE providing Responsive Reserve and/or Regulation Services must provide communications equipment to receive ERCOT telemetered control deployments.

Any QSE providing Regulation Service must provide appropriate Real Time feedback signals to report the control actions allocated to that QSE’s Generation Resources.

Any QSE that represents a provider of Responsive Reserve, Non-Spinning Reserve, or Replacement Reserve Services using Load acting as a Resource shall provide separate telemetry of the real power consumption of each Load providing the above Ancillary Services and the status of the breaker controlling that Load.  If Load is used as a Responsive Reserve Resource, the status of the high-set under frequency relay will also be telemetered.

Real Time data for reliability purposes must be accurate to within three percent (3%). This telemetry may be provided from relaying accuracy instrumentation transformers.

#### 3.1.3.2	Daily Resource Plan

Reference:  Protocols, Section 4.4.15, QSE Resource Plans

4.4.15	QSE Resource Plans

Each QSE that represents a Resource will present a Resource Plan to ERCOT at 1600.  These Resources may be specific generating units and/or Load acting as a Resource.  The Resource Plan capacity should be sufficient to accommodate the combined quantity of energy and Ancillary Services scheduled by that QSE from the Resources that the QSE represents.  The Resource Plan shall indicate the availability of the Resources represented by the QSE and the planned operating level of each Resource, for each hour of the Operating Day.  The Resource Plan shall indicate the High Operating Limit and Low Operating Limit by Resource.  A Resource may be listed as unavailable to ERCOT if the Resource’s capacity has been committed to markets in regions outside of ERCOT.

QSEs shall use best efforts, consistent with Good Utility Practice, to continually update their Resource Plans to reflect the current and anticipated operating conditions of the Resources.  ERCOT will monitor the performance of QSEs with respect to the submission of accurate Resource Plans.  ERCOT will work with individual QSEs as necessary to improve the individual QSE performance.

[PRR359:  Replace Subsection 4.4.15, QSE Resource Plans as follows when the system change is implemented.]

Each QSE that represents a Resource will present a Resource Plan to ERCOT at 1600.  These Resources may be specific generating units and/or Load acting as a Resource.  The Resource Plan capacity should be sufficient to accommodate the combined quantity of energy and Ancillary Services scheduled by that QSE from the Resources that the QSE represents.  The Resource Plan shall indicate the availability of the Resources represented by the QSE, including a lead-time status code, and the planned operating level of each Resource, for each hour of the Operating Day.  The Resource Plan shall indicate the High and Low Operating Limits, and High and Low Sustainable Limits by Resource.  A Resource may be listed as unavailable to ERCOT if the Resource’s capacity has been committed to markets in regions outside of ERCOT.

[PRR423:  Add the following sentence to the end of the first paragraph of 4.4.15, QSE Resource Plans, when the system change is implemented.  If PRR423 is implemented before PRR359, add this sentence both to the end of the first paragraph of 4.4.15, QSE Resource Plans, and the end of the PRR359 box above.]

- Each QSE that represents a Resource, either Load acting as a Resource or Generation, shall submit to the ERCOT Control Area Authority, by 1600 hours each day, their Resource Plan for the next day.

The capacity of all Resources shown as available in the Resource Plan should be sufficient to accommodate the combined quantity of energy and Ancillary Services scheduled by that QSE from the Resources which the QSE represents.

The Resource Plan shall indicate the availability of all Resources represented by the QSE and the planned operating level of each Resource, for each hour of the Operating Day.

The Resource Plan shall indicate the High and Low Operating Limits, and High and Low Sustainable Limits, of each Resource.

A Resource may be listed as unavailable to ERCOT if the Resource’s capacity has been committed to markets in regions outside of ERCOT.

The QSE representing the Resource will report to ERCOT any changes in Resource status by updating its Resource Plan before the beginning of the next hour following the change in status.

#### 3.1.3.3	Unplanned Load Changes

Reference:  Protocols, Section 5.5.1, Changes in Resource Status

5.5.1	Changes in Resource Status {States in Part…}

The QSE will notify ERCOT of an unplanned change in Resource status as soon as practicable following the change.  The QSE representing the Resource will report any changes in Resource status to ERCOT in the Resource Plan by the beginning of the next hour following the change in status.

The QSE shall notify ERCOT Control Area Authority of an unplanned change in Load Resource status as soon as practical following the event.

The QSE representing the Load that is to be used as a Resource shall provide ERCOT Control Area Authority with an update of the Load status.  The update will be provided in the Resource Plan by the beginning of the next hour following the change in status.

Each QSE shall call on Resources from which commitments have been made to provide Ancillary Services.

#### 3.1.3.4	QSE Responsibility for Department of Energy (DOE) and NERC Reportable Events

QSEs shall provide ERCOT System Operations with the DOE Form EIA-417 report for each DOE reportable event that occurred in areas they represent.  ERCOT, as the Control Area Authority, will forward these reports to the DOE and NERC as required.

### 3.1.4	Power Generation Companies

This Section defines the minimum requirements for the integration of Generation Resources that are 10 MW or greater into the ERCOT System.

Each Generation Resource shall meet the following general requirements in order to integrate into the ERCOT System.

- Physically located in the ERCOT Control Area; and

- Represented by a QSE represented PGC, or directly by a QSE.

A QSE shall be the reporting Entity for a PGC and shall communicate with both ERCOT Control Area Authority and the TDSP maintaining the PGCs connection.

The QSE reporting for a PGC or a Generation Resource shall provide the following telemeter quantities for Generation Resources greater than ten (10) MW to ERCOT Control Area Authority:

- Generator megawatts;

- Generator megavars;

- Generator energy (megawatt-hours);

- Substation equipment status; and

- Voltage where the Facility connects to the Transmission Grid;

- The directly connected TDSP may obtain any required data from ERCOT.

These quantities are fully described in Operating Guide 2.

The QSE representing the PGC shall provide a separate, dedicated and reliable communications voice channel and data communications to each of ERCOT Control Area Authority and the directly connected TDSP.

The QSE representing the PGC shall, as a minimum, provide adequate modeling information, as follows:

- Machine impedance and characteristics;

- Excitation system data, governor system constants;

- Transformer impedance; and

- Other relevant information.

This information is necessary to support ERCOT and TDSP’s ability to perform operational and planning studies such as:

- Transient and Dynamic Stability;

- Short Circuit;

- Load Flow; and

- Reliability Evaluations.

When in operation, the Generation Resource greater than ten (10) MW shall be staffed or monitored twenty four (24) hours per day, by personnel capable of making operating decisions and possessing the ability to control the Generation Resource output when requested by the representing QSE or the directly connected TDSP during Black Start procedures.

The Generation Resource shall perform maintenance, start-up, and operation in a reliable and safe manner consistent with Good Utility Practices.

The Generation Resource shall implement the following in a reliable and safe manner and in accordance with the switching procedure of the directly connected TDSP:

- Synchronizing of the generation to the ERCOT System; and

- Transmission switchyard switching or clearances.

The operation of a Generation Resource shall conform to the requirements of ERCOT or NERC Operating Criteria, Guide, or Standard.

#### 3.1.4.1	Federally Licensed PGCs

The Resource generating Facility licensed by a federal regulatory agency shall, through its QSE representative, provide any applicable grid interconnection and performance licensing requirements to ERCOT and the TDSP to which the licensee is connected.

The TDSP is obligated to incorporate any such licensing requirements into its planning and operations, and the ERCOT Control Area Authority shall support such requirements. Both ERCOT and the TDSP will create necessary procedures for satisfying these requirements. Such procedures will include provisions to notify the Facility licensee through it’s QSE of any requirements that cannot be satisfied.

Any proposal for revision of this Operating Guide and the procedures incorporating the licensee requirements that would diminish the Obligation or ability of ERCOT or the TDSP to support these requirements shall be provided to the licensee through it’s QSE to afford it an opportunity for review and response.  Any such proposal that is approved, as a result of which the licensee is required to implement changes to meet its license requirements or to seek amendment to its license, shall become effective no sooner than six (6) months following the approval.

#### 3.1.4.2	PGC Data Reporting

The PGC’s reporting QSE shall provide the following information to ERCOT Control Area Authority at the times specified:

| TIME | INFORMATION |
| --- | --- |
| Every 10 seconds | - Generation net MW output; - Generation net MVAR; - Status of switching devices in switchyard; - Generating unit breaker status; - Generating unit High Operating Limit; and - Generating unit Low Operating Limit. |
| Daily | - Planned unit status; - Planned unit capability (both hourly and daily), and - Fuel limitations. The reporting Entity will promptly report this condition to ERCOT Control Area Authority. |
| Annually | - Seasonal capability where applicable; and - Planned maintenance schedules. This information shall be updated when it changes. |

Each Generator at a Generation Resource shall have an automatic speed governor in service while the Generator is On-line.  Testing and regulation performance of the speed governor shall be in accordance with Operating Guide Section 6.2.1, Turbine Governor Speed Regulation Tests.  The Generator is required to notify the ERCOT Control Area Authority, through its QSE if the operation of speed governors is impaired.

Each Generation Resource providing an Ancillary Service shall provide output consistent with the requirements of that Ancillary Service and ERCOT instructions.

In the event of an ERCOT declared emergency, ERCOT may require the QSE to notify the appropriate Generation Resource and increase or decrease generation and/or change the voltage and reactive requirements in accordance with the Protocols.  The Generation Resource shall use its best efforts in meeting these required output levels in order that the ERCOT System can maintain safe and reliable operation.

It is the responsibility of ERCOT, TDSP, and QSE to ensure that all Generators carry an operational share of reactive support to insure adequate and safe Voltage Profiles are maintained in all areas of ERCOT.  To accomplish this, the following requirements shall apply to each Generation Resource:

- Each Generation Resource shall have Automatic Voltage Regulators and power system stabilizers in service as defined in Section 3.1.4.5, Automatic Voltage Regulators And Power System Stabilizers, below.

- The Generation Resource shall be designed and operated consistent with its obligations to Supply Voltage Ancillary Service as required in the ERCOT Protocols and ERCOT Control Area Authority Procedures.

- ERCOT and the designated TDSP have the right and Obligation to Dispatch the reactive output (VARS) of each Generation Resource within its design capability to maintain adequate transmission voltage in ERCOT.

- ERCOT and the TSP shall be notified of any equipment changes that affect the reactive capability of an operating generating unit no less than 60 days prior to implementation of the changes, and any such changes that decrease the reactive capability of the generating unit below the required level must be approved by ERCOT prior to implementation.

- High reactive loading or reactive oscillations on generation units should be communicated to the QSE, the Transmission Operator, and ERCOT as soon as practicable.

- The tripping off line of a generating unit due to voltage or reactive problems should be reported to ERCOT, the Transmission Operator, and the QSE as soon as practicable.

#### 3.1.4.3	Unit Capability Testing Requirement

Reference:  Protocols, Section 6.10.2, General Capacity Testing Requirements

6.10.2	General Capacity Testing Requirements

QSEs shall provide ERCOT a list identifying each Generation Resource unit that is expected to operate more than one hundred sixty eight (168) hours in a Season as a provider of energy and/or Ancillary Services.  ERCOT shall evaluate, during each Season of expected operation, the Net Dependable Capability of each unit expected to operate more than one hundred sixty eight (168) hours during that Season, except for any Generation Resources used solely for energy services and whose capacity is less than ten (10) MW.  Prior to the beginning of each Season, QSEs shall identify the Generation Resources to be tested during the Season and the specific week of the test if known.  This schedule may be modified by the QSE (including retests) during the Season.  QSEs not identifying a specific week for a Generation Resource unit test must test the unit within the first one hundred sixty eight (168) hours of run time during the Season or operate with a Net Dependable Capability equal to the highest integrated hourly MWh output demonstrated during the first one hundred sixty eight (168) hours of run time.  QSEs do not have to bring units On-line or shut down solely for the purpose of the seasonal verification.  Any unit for which the QSE desires qualification to provide Ancillary Services shall have its Net Dependable Capability verified prior to providing services using the Generation Resource unit even if it fits the less than one hundred sixty eight (168) hour or small capacity exception.  The capability of hydro units operating in the synchronous condenser fast response mode to provide hydro Responsive Reserve shall be evaluated by Season.

Load acting as a Resource to provide Ancillary Services shall have its telemetry attributes verified by ERCOT annually.  In addition, once every two (2) years, any LaaR providing Responsive Reserve Service shall test the under frequency relay or the output from the solid-state switch, whichever applies, for correct operation.  However, if the Load’s performance has been verified through response to an actual event, the data from the event can be used to meet the annual telemetry verification requirement for that year and/or the biennial relay testing requirement.

#### 3.1.4.4	Unit Reactive Capability Testing and AVR Testing

Reference:  Protocols, Section 6.10.3.5, Reactive Supply from Generation Resources required to provide VSS

6.10.3.5	Reactive Supply from Generation Resources

(1)	The Generation Entity must verify and maintain its stated Reactive Power capacity for each of its Generation Resources, as required by the NERC Planning Standards “System Modeling Data Requirements, Generation Equipment.” Sections 2.B, Measurement 3 and as may be required by the Operating Guides. Generation Resources reactive capability limits shall be specified considering nominal substation voltage.

(2)	The Generation Entity will conduct reactive capacity qualification tests to verify the maximum leading and lagging reactive capacity of all Generation Resources.  Reactive capacity tests will be performed on initial qualification and periodically at an ERCOT-set interval no more often than once every two years, unless ERCOT has information indicating that current data is inaccurate. The Generation Entity is not obligated to place Generation Resources on line solely for testing.  The reactive capacity tests are run at a time agreed on in advance by the Generation Entity, its QSE, the applicable TDSP, and ERCOT.

(3)	Maximum lagging power factor reactive operating limit shall be demonstrated during peak Load Season, at the net dependable megawatt capability, insofar as system voltage conditions and other factors will allow.  The Generation Resource should be required to maintain this level of reactive power for at least fifteen (15) minutes.

(4)	Maximum leading power factor reactive operating limit shall be demonstrated during light Load conditions, with the unit operating at its minimum Load, insofar as system voltage conditions and other factors will allow.  The unit should be required to maintain this level of Reactive Power for at least fifteen (15) minutes.

(5)	The Generation Entity shall perform the unit automatic voltage regulator (AVR) tests and shall supply AVR data as required by the NERC Planning Standards “System Modeling Data Requirements, Generation Equipment.”  Sections 2B, Measurement 4, and 2B, Measurement 6 and as may be specified in the Operating Guides. The AVR tests will be performed on initial qualification and periodically at an ERCOT-set interval no more often than once every five years.  The AVR tests are run at a time agreed on in advance by the Generation Entity, its QSE, the applicable TDSP, and ERCOT.

Generation Resources shall conduct generating unit reactive capability tests as specified in ERCOT Protocols and Operating Guides.  Test results shall be reported to ERCOT who shall forward them to the TSPs.  If reactive output of the generating units is limited by transmission system conditions during the tests, this shall be noted on the test report.

Performance tests shall be conducted on Automatic Voltage Regulators every five years or if equipment characteristics are knowingly modified.  The test reports should include the minimum and maximum excitation limiters, volts/hertz settings, gain and time constants, type of voltage regulator control function, date tested, and voltage regulator control setting.

Excitation systems, including power system stabilizers, shall also be tested every five (5) years.

3.1.4.5	Turbine Governor Speed Testing

Governor performance tests should be conducted at least every two years and results used in analysis as described in Section 6.2.1, Turbine Governor Speed Regulation Tests.  A sample of such tests may be found in Section 6.2.1.2, Example of a Turbine Governor Speed Regulation Test for Mechanical Hydraulic Governor.

3.1.4.6	Enforcement of Testing Requirements

Enforcement Of AVR Testing

#### ERCOT Compliance templates, available on ERCOT website, specify enforcement rules.

#### 3.1.4.7	Automatic Voltage Regulators And Power System Stabilizers

Generator Automatic Voltage Regulators and power system stabilizers will be kept in service whenever possible.  Generation Entities shall notify their QSE, who in turn will promptly notify the ERCOT Control Area Authority by telephone of the circumstances, when a voltage regulator or stabilizer is unavailable due to maintenance or failure and when it is returned to normal operation.

Unit AVR and PSS modeling information required in the ERCOT Planning Criteria shall be determined from actual unit testing described in the Operating Guides.  Within thirty (30) days of ERCOT’s request, the results of the latest test performed shall be supplied to ERCOT and the TSP.

#### 3.1.4.8	Protective Relaying Requirement

The Facility’s generation machine characteristics and plant design shall incorporate the under-frequency firm Load shedding philosophy and criteria defined in Operating Guide 2.9. Requirements for Under-Frequency Relaying.  Inherent in this philosophy is the idea that all generators remain on line until all three steps of firm Load shedding have been executed.

The generation Facility shall have protective relaying necessary to protect its equipment from abnormal conditions as well as to be consistent with protective relaying criteria as described in Operating Guide Section 5: Planning.

Within thirty (30) days of ERCOT’s request, Generation Resources shall provide ERCOT with the operating characteristics of any generating unit’s equipment protective relay system or controls that may respond to temporary excursions in voltage with actions that could lead to tripping of the generating unit.

Generating Resources required to provide VSS shall have and maintain the following capability:

(1)	Over-excitation limiters shall be provided and coordinated with the thermal capability of the generator field winding and protective relays in order to permit short-term reactive capability that allows at least eighty percent (80%) of the unit design standard (ANSI C50.13-1989), as follows:

Time (seconds)		10	30	60	120

Field Voltage %		208	146	125	112

After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.

(2)	Under-excitation limiters shall be provided and coordinated with loss-of-field protection to eliminate unnecessary generating unit disconnection as a result of operator error or equipment misoperation.

#### 3.1.4.9	Outages

Generation Resource Outage

See Section

Forced Outages

The Control Area Authority shall be notified of the Forced Outages of any Resource within one (1) minute.???????without telemetry?????

Sabotage Information Exchange

See Section 2.7.2.3, Sabotage Information Exchange.

3.1.4.10	Enforcement of Load acting as a Resource (LaaR) Testing Requirement

After initial qualification, a LaaR’s telemetry and any applicable relay functionality will be tested and validated by ERCOT within twenty-four (24) months as specified in these Operating Guides.  If a LaaR fails to provide the appropriate documents as required in the annual and biennial verification test for two (2) consecutive years, ERCOT shall notify the associated QSE of any noncompliance.  After a thirty (30) day allowance for the deficiency to be corrected, ERCOT shall reduce the Resource’s ability to provide Ancillary Services in the ERCOT market to zero.

### 3.1.5	Transmission and/or Distribution Service Providers

Reference:  Protocols, Section 5.5.2, Changes in Transmission Facility Status

5.5.2	Changes in Transmission Facility Status

The TDSP will notify ERCOT of any changes in status of Transmission Facility elements as provided and clarified in the ERCOT procedures.  The TDSP will notify ERCOT of any other Transmission Facility status as soon as practicable following the change.  In addition, any short-term inability to meet minimum TSP or DSP reactive requirements shall be immediately reported to ERCOT by way of the TSP.

Reference:  Protocols, Section 6.4.2, Determination of ERCOT Control Area Requirements

6.4.2	Determination of ERCOT Control Area Requirements {States in Part…}

(6)	Voltage Support:  ERCOT in coordination with the TDSPs shall conduct studies to determine the normally desired Voltage Profile for all Generation Resource busses in the ERCOT System and shall post all Voltage Profiles on the Market Information System.  ERCOT may temporarily modify its requirements based on current system conditions.  ERCOT shall determine the amount of Voltage Support Service needed to provide sufficient reactive capacity in appropriate locations to provide ERCOT System security as specified in the Operating Guides.

6.5.7	Voltage Support Service

(1)	A QSE’s Generation Resource is expected to operate within the reactive power capability requirements specified in these Protocols and the Operating Guides.

(2)	A QSE’s Generation Resource must be capable of maintaining a Voltage Profile limited to the quantity of Reactive Power the Generation Resource can produce at rated capability, (MW), and a power factor of .95 leading or lagging measured at the unit main transformer high voltage terminals. This quantity of Reactive Power is the Unit Reactive Limit (URL).

(6)	ERCOT shall establish, and update as necessary, Voltage Profiles at points of interconnection of Generation Resources to maintain system voltages within established limits

(8)	ERCOT shall deploy static Reactive Power Resources as required to continuously maintain dynamic Reactive Reserves from QSEs, both leading and lagging, adequate to meet ERCOT System requirements.

(10)	QSEs shall meet, within established tolerances, and respond to changes in the Voltage Profile established by ERCOT subject to the stated QSE Reactive Power and actual power operating characteristic limits and voltage limits.

6.5.7	Voltage Support Service

All Generation Resources (including self-serve generating units) that have a gross generating unit rating greater than twenty (20) MVA or those units connected to the same transmission bus that have gross generating unit ratings aggregating to greater than twenty (20) MVA, that supply power to the ERCOT Transmission Grid, shall provide Voltage Support Service.

6.7.6	Deployment of Voltage Support Service {States in Part…}

(2)	ERCOT and TDSPs shall develop operating procedures specifying Voltage Profiles of transmission controlled reactive Resources to minimize the dependence on generation-supplied reactive Resources.  For Generation Resources required to provide VSS, step-up transformer tap settings will be managed to maximize the use of the ERCOT System for all Market Participants while maintaining adequate reliability.

ERCOT and TDSPs shall operate the ERCOT Interconnected System in compliance with Good Utility Practice and NERC and ERCOT standards, policies, guidelines and operating procedures.

TDSPs monitoring system conditions shall notify ERCOT when Transmission Facility Elements approach operating limits as soon as practicable, if these Transmission Facility Elements will affect the ERCOT System.

A TDSP shall notify ERCOT Control Area Authority of any changes in their transmission Facility status within 10 seconds of the change of status.

TDSPs shall follow ERCOT instructions related to ERCOT responsibilities:

- Performing the physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, protective relays, metering and Load shedding equipment;

- Directing changes in the operation of transmission voltage control equipment;

- TDSPs will maintain voltage set points established by ERCOT utilizing static reactive devices.  TDSPs, under the direction of ERCOT, will coordinate TDSP static device switching with QSE dynamic reactive device operation.  Static reactive devices will be brought on line before predicted daily maximum Load growth or dynamic reactive Resources reach operating limits.  Static reactive devices will be taken off line during daily load decline and before dynamic reactive Resources reach operating limits.  ERCOT will coordinate Automatic Voltage Regulator, dynamic and static reactive device outages to ensure adequate Reactive Reserves are maintained; and

- Taking those additional actions required to prevent an imminent Emergency Condition or to restore the ERCOT Transmission Grid to a secure state in the event of an ERCOT System Emergency.

Each TDSP, at its own expense, may obtain Operating Period data from ERCOT (See Section 2.3.1, above).

#### 3.1.5.1	Transmission Operator Responsibility for Department of Energy (DOE) and NERC Reportable Events

TOs shall provide ERCOT System Operations with the DOE Form EIA-417 report for each DOE reportable event that occurred in areas they represent.  ERCOT, as the Control Area Authority, will forward these reports to the DOE and NERC as required.

#### 3.1.5.2	Outages

Forced Outages

Forced Outages of all transmission lines (>60 kV) shall be reported to ERCOT Control Area Authority immediately.

Forced Outages of other transmission equipment that affect power flows or transfer capacity will be reported immediately to ERCOT Control Area Authority.

When a Forced Outage affects the overall security or capacity, ERCOT shall take remedial steps immediately to ensure that other Facilities are not loaded beyond capacity limits.

The TDSP may remove equipment that poses a threat to personnel or Facilities from service immediately and notify ERCOT of its action.

Scheduled Outages

When a transmission line (>60 kV) is out of service the capacity of ERCOT transmission lines should not be exceeded under normal or single contingency conditions.

TSPs shall communicate the Scheduled Outage information to the appropriate Distribution Service Providers.

Sabotage Information Exchange

See Section 2.7.2.3 Sabotage Information Exchange

### 3.1.6	Responsibility For Equipment Ratings

TDSPs are responsible for determining the rating of their Facilities.

Technical limits established for the operation of transmission equipment shall be applied consistently in TTC calculations, Engineering Studies, Real Time security analyses, and operator actions.

TDSP’s shall provide ERCOT with three (3) nominal Transmission Facility Ratings:

- Continuous Rating:  Represents the continuous MVA rating of a Transmission Facility (including substation terminal equipment in series with a conductor or transformer) at the applicable ambient temperature.  The Transmission Facility can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

- Emergency Rating:  Represents the two (2) hour MVA rating of a Transmission Facility (including substation terminal equipment in series with a conductor or transformer) at the applicable ambient temperature.  The Transmission Facility can operate at this rating for two (2) hours without violation of NESC clearances or equipment failure.

- Fifteen Minute Rating:  Represents the fifteen (15) minute MVA rating of a Transmission Facility (including substation terminal equipment in series with a conductor or transformer) at the applicable ambient temperature and with a step increase from a prior loading of ninety percent (90%) of the Continuous Rating.  The Transmission Facility can operate at this rating for fifteen (15) minutes, assuming its pre-contingency loading was ninety percent (90%) of the Continuous Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure.  This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current.

- In operating the Transmission Grid, ERCOT shall use these ratings as follows:

- ERCOT shall limit pre-contingency flows to enforce the Continuous Rating.

- If  a valid Remedial Action Plan  is unavailable to unload  the Transmission Facility post contingency or the pre-contingency loading is greater than ninety percent (90%) of the Continuous Rating, ERCOT shall enforce pre-contingency System Operating Limit(s) to control the post contingency loading of the facility to levels below the Emergency Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Continuous Rating within two (2) hours.

- If a Remedial Action Plan is documented at ERCOT to relieve the loading on the  Transmission Facility within fifteen (15) minutes; ERCOT shall enforce pre-contingency System Operating Limit(s) to control the post contingency loading of the facility to levels below the Fifteen Minute Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Emergency Rating within fifteen (15) minutes.

- ERCOT shall use best efforts to restore all Transmission Facilities to within Continuous Ratings as soon as practicable, based on Good Utility Practice.

## 3.2	Scheduling Interfaces with ERCOT

### 3.2.1	Reserved

### 3.2.2	Scheduling Process

#### 3.2.2.1	Day Ahead Scheduling

Reference:  Protocols, Section 4.1.1, Day Ahead Scheduling Process, and Operating Guides Section 2.5.1

| Time Period at or before: | Qualified Scheduling Entity (QSE) Submission: | ERCOT Action: |
| --- | --- | --- |
| Day Ahead |  |  |
| 0600 |  | - Publish updated transmission system information, Load Forecasts (Congestion Zone, and by total ERCOT Transmission System), Ancillary Service (AS) Plan, AS responsibility, mandatory decremental Balancing Energy Service bid percentage requirements and Transmission Loss Factors and Distribution Loss Factors. |
| 1100 | - Balanced Energy Schedule of Obligations and Resources. - Self-Arranged AS Schedule. | - Validate Schedules and notify affected Qualified Scheduling Entities (QSEs) of any invalid or mismatched schedules. |
| 1115 | - Resubmit corrected schedules. | - Review Schedules: Commercial Model. - CSC Congestion. - Notify QSEs of Congested CSCs. - Post schedule impact on CSCs. - Notify QSEs of any difference in ERCOT’s zonal Load forecast and the aggregate of QSE schedules in a zone. |
| 1300 | - Update Balanced Energy Schedule of Obligations and Resources. - Update Self-Arranged AS schedule - AS bids to Supply AS to ERCOT AS Market. | - Validate Schedules and notify affected QSEs of any invalid or mismatched schedules. |
| 1315 | - Resubmit corrected updated schedules. | - Validate resubmitted schedules and adjust as necessary. |
| 1330 |  | - Purchase AS through ERCOT AS Market in order to complete ERCOT’s Day Ahead AS plan. - Review Day Ahead Market Clearing Prices for Capacity (MCPC) for each Day Ahead AS market operated by ERCOT. |
| 1500 | - Submit updated AS schedule that includes Self-Arranged and AS bids selected by ERCOT. | - Review and validate AS schedules as necessary. |
| 1600 | - Submit Resource Plans with unit-specific information. - Submit Replacement Reserve Service (RPRS) Bids. | - Verify that Resource Plans are sufficient to meet the QSE schedule. If not, ERCOT will notify the QSE. |
| By 1800 |  | - Evaluate Resource Plans to determine system security. - Evaluate RPRS needed to correct CSC, and Operational Congestion – Operational Model, and capacity insufficiency. |
| By 1800 |  | - Create Merit Order of RPRS by Zone or Operational Constraint as applicable. |
| By 1800 |  | - Determine MCPC for RPRS by Zone as applicable. |
| By 1800 |  | - Close and clear Day Ahead RPRS market. |
| After 1800 | - Modify RPRS bids. |  |

#### 3.2.2.2	Adjustment Period Scheduling

Reference:  Protocols, Section 4.1.2, Adjustment Period Scheduling Process

4.1.2	Adjustment Period Scheduling Process

The Adjustment Period Scheduling Process will follow the following timeline with time T being the start of the Operating Hour:

| Adjustment Period | QSE Responsibility: | ERCOT Responsibility: |
| --- | --- | --- |
| Time = T minus 60 minutes | - Submit updated Balanced Schedule of Obligations and Supply for the hour beginning at Time T, and any hour after T. - Submit bids for Balancing Energy including any mandatory decremental Balancing Energy bids. - Submit updated Self-Arranged AS schedule for the hour beginning at Time T and any hour after Time T (the amount of Self-Arranged AS may not change from Day Ahead, however, the Resources supplying the Self Arranged AS may be altered. If ERCOT calls on additional AS in the AP, the allocated portion of the additional AS may be self- arranged). - Submit updates to Resource Plan. - Submit bids for RPRS. - Submit bids for additional Ancillary Services. - Submit bids for incremental and decremental Resource specific premiums. | - Review updated Balanced Schedule. - Review updated Resource Plans. - Review updated Self-Arranged AS Schedule. - Validate Schedules and notify affected Qualified Scheduling Entities (QSEs) of any invalid or mismatched schedules. - Identify CSC or OC Congestion or capacity insufficiency. |
| Time = T minus 45 minutes | - Resubmit corrected schedules. |  |

### 3.2.3	Procurement of Replacement Reserve Service Resources

The typical RPRS procurement process will adhere to the following timeline:

| RPRS PROCUREMENT PROCESS | QSE RESPONSIBILITY |
| --- | --- |
| Time X | Submit or update bids for RPRS |
| Time X plus 60 minutes | Update Balanced Schedules |
| Time X plus 75 minutes | Resubmit corrected schedules. |

Time X is the start of a clock hour when ERCOT identifies Zonal and Local Congestion, or capacity insufficiency.

Time X can be the start of any clock hour during the Adjustment Period but cannot be less than 2 hours prior to the Operating Hour that energy from the RPRS unit is required.

RPRS bids remain active until withdrawn by the QSE.

### 3.2.4	Procurement of Additional Ancillary Services

The Adjustment Period AS procurement process for RRS, NSRS and RGS will use the following timeline with time X being the start of a clock hour when ERCOT identifies the need for additional AS.  Time X can be the start of any clock hour during the Adjustment Period but cannot be less than 2 hours prior to the Operating Hour that the additional AS capacity is required.

| ADDITIONAL AS PROCUREMENT PROCESS | QSE RESPONSIBILITY |
| --- | --- |
| Time X | Submit or update bids for RRS, NSRS and RGS |
| Time X plus 60 minutes | Update their Balanced Schedules, including additional Self-Arranged AS. Remove the portion of the bid, submitted by Time X, that are to be used in incremental self-arrangement and bilateral AS sales, if desired. |
| Time X plus 75 minutes | Resubmit corrected schedules. |

## 3.3	Document Control

Authorities

| Prepared by | Date Completed | Reviewed by | Date Authorized |
| --- | --- | --- | --- |
| B. Garza | April 17, 2001 | ROS |  |
| I. Flores | April 15, 2002 | OGRTF/ROS |  |
| I. Flores | 30 September 2002 | OGRTF/ROS |  |
| I. Flores | 1 December 2002 | OGRTF/ROS |  |
| I. Flores | 1 January 2003 | OGRTF/ROS |  |
| I. Flores | 1 April 2003 | OGRTF/ROS |  |
| J. Gilbertson | 29 August 2003 |  |  |

Distribution List

| Name | Organization |
| --- | --- |
| Reliability Operations Subcommittee | Technical Advisory Committee |

Change History

| Issue/Date | Reason for issue |
| --- | --- |
| Version 1.0 February 28, 2001 | Updated from Working Group comments. Submitted to Technical Advisory Committee to approve handover to the Reliability Operating Subcommittee |
| Version 1.0a March 2, 2001 | Inserted sections 3.2.4.2 – 3.2.4.4 |
| Version 1.1 April 16, 2001 | Clarified sections 3.2.4.2 – 3.2.4.4 |
| May 1, 2002 | OGRR101 |
| October 1, 2002 | OGRR113 |
| December 1, 2002 | OGRRs 114 & 116. Revised Sections 3.1.4.2, 3.1.4.3, 3.1.3.2 & 3.2.2.1 to match the Protocols references. |
| January 1, 2003 | OGRR119, revised Section 3.1.3.1 to add a backup plan requirement for QSEs. |
| April 1, 2003 | OGRR125 – updated Protocols referenced in Sections 3.1.3.2, 3.2.1.2, 3.2.2.1 & 3.2.6. OGRR126 – updated reference in Section 3.2.6 citing Protocols Sections 4.9.1. 4.9.2 & 4.9.3 and deleted redundant text after reference. |
| September 1, 2003 | OGRR130 – revised Section 3.1.4.1 & 3.1.4.5. OGRR134 – revised Section 3.1.6. |

Note that it is allowed by these guides and Protocols for the QSE to submit the maximum generation within a one hundred sixty eight (168) hour period and submit without any special testing effort.  A form is provided within these guides for submission of test results.