State Estimator Observability and Redundancy Requirements

A proposal submitted by ERCOT staff to the Reliability and Operations Subcommittee

September 7, 2004

Purpose

Executive Summary

- Introduction

  - Operating States of a Power System

  - Why State Estimator?

  - Why RTCA? (Real time Contingency Analysis)

  - Model of ERCOT System

  - Cost vs ERCOT Responsibility

- Observability Analysis – How and Results

- Redundancy and Critical Measurements

- Topology, Validity and Availability

- Observability Requirement & available exceptions

6.   Redundancy Standard and Exceptions

Appendix 1

- State Estimator basics

  - Network Topology processing (NTP)

  - Measurement Consistency Checking

  - Observability Analysis

  - WLS State Estimator

  - Bad Data Detection and Filtering

- Topology Estimator

- Time Schedule Model Implementations

- Manual Interventions in the state estimator

Appendix 2

Observability and Optimal RTU Placement

Appendix 3

RTU Placement Results

Purpose

Over the last year ERCOT has implemented the use of Real Time Contingency Analysis (RTCA) as the primary real-time reliability tool for transmission security.  This tool is highly dependent upon the accuracy of the State Estimator solution.  As experience has accumulated in the use of this tool, it has become evident that in areas of low observability, or low redundancy, RTCA can indicate a need to constrain generation which may not be supported by subsequent analysis.

NERC rules and ERCOT guides do not permit ERCOT to ignore a security/reliability violation; so reducing or eliminating these areas of unobservability has become a priority at ERCOT.

In parallel with our growing experience, ERCOT subcommittees have advanced a proposal to convert the ERCOT market to a Nodal pricing scheme. Several of these proposals are centered upon a successful State Estimator implementation.

In response to one of the proposals at these subcommittees, a white paper, entitled 
Telemetry Addendum” was proposed.  In this paper, it was stated that:

“ROS will coordinate with WMS to ensure a common understanding of the level of State Estimator performance required to calculate “reasonably accurate LMPs.”  The State Estimator performance standard shall define the performance requirements necessary to provide State Estimator results within a desired level of confidence and the calculation of reasonably accurate LMPs.  Further, this standard shall address the State Estimator’s ability to detect, correct, and/or otherwise accommodate communications systems failures, failed data points, and missing or inaccurate measurements.”

The existence of this paper was communicated to the Board of Directors on May 18th, 2004.

At its July 13th meeting, in response to this paper, the ROS and ERCOT agreed that ERCOT staff would prepare a draft “Strawman” document describing the technical requirements for data needed for the function of the ERCOT State Estimator.  ERCOT suggested that a workshop on State Estimator be held in order to ensure that all the relevant topics were addressed.

ERCOT held two workshops on June 22nd and July 15th to explain its State Estimator methodology and usage and to invite participants to share their related concerns.

This document was prepared in response to the ROS agreement.  The document proposes definitions of the required operability and redundancy of telemetry in ERCOT, and explains the proposed levels of observability, redundancy, and analysis to be established for the data requirements for the ERCOT State Estimator.

Executive Summary

The State Estimator is a real-time application used to more accurately and consistently determine the operating state of a large power system. Accurate modeling of the transmission network and sufficient accurate telemetry are vital to this tool.

Maintaining a successful state estimator requires continuous monitoring and management of the validity of thousands of individual measurements.  This process is complicated in ERCOT by daily topology changes to the transmission network and accompanying updates to the Network Model at least weekly.

ERCOT is striving to meet the process challenges with an appropriate level of effort; however, ERCOT cannot resolve all issues without coordination with the Transmission Service Providers.

This paper addresses the methodologies ERCOT is to use in determining data required from Transmission Service Providers.

ERCOT proposes a standard that requires observability for all buses which cannot be demonstrated un-necessary to detecting post-contingency overloads.  An exception process for demonstrating which bus measurements are un-necessary is proposed and discussed.

ERCOT also proposes and discusses a standard of redundancy which requires redundant measurements at critical locations.

ERCOT staff recommends that this standard be adopted with or without the proposed implementation of nodal pricing in the ERCOT service area.

A summary of these requirements is shown below.

|  | Standard | Exceptions |
| --- | --- | --- |
| Observability | All busses 69kV and above unless an exception applies | A bus measurement may be exempted if that measurement can be shown, through network analysis, not needed to calculate any pre- or post-contingency overrating or over limit violation which may result when generation patterns are varied. |
| Redundancy | Redundancy required for all 345 kV buses and selected 138 kV buses related to critical circuits. Only those 69 kV facilities which are known to, or which may be observed to, have reliability or significant economic impact may be considered for redundancy. Otherwise, 69 kV facilities measurements will be backed up by primitive model values. | -If demonstrated non-critical -If frequent failure mechanism is corrected. |

1. Introduction

1.1 Operating States of a Power System

The operating conditions of a power system at a given point in time may be determined if the network model and complex phasor voltages at every system bus are known. Since a system may be fully defined by the full set of complex phasor voltages, the set of phasor voltages for all buses in a transmission network is referred to as the state of the system. A transmission system may be operating in one of four possible states; namely, secure, insecure, emergency and restorative as operating conditions change.

A power system is said to operate in a secure state if all the loads in the system can be supplied by the on-line generators without violating any operational constraints (i.e. facility ratings and System Operating Limits (SOL)) and if the system can remain in a normal state following the occurrence of any defined contingency.

Secure

Restorative

Emergency

Insecure

Changing Conditions

Contingency

Outage

Re-posturing of

Transmission System

Restoration of

Contingency, load,

etc.

Note- A Restorative State is a

Secure state, but all load may

not be served.

A state for a transmission interconnection is said to be insecure if the power balance at each bus and all operating inequality constraints are still satisfied, yet the system remains vulnerable with respect to one or more of the considered contingencies. If the system is found to be in a within normal SOLs, but in an insecure operating state, then preventive actions including, but not limited to, re-dispatch of resources, operational switching actions, or other similar actions should be taken to re-position  the system and avoid exposure to a  move into an emergency state.

Operating conditions may change significantly to cause violation of SOLs.  In such a situation, the system is said to be operating in an emergency state. Operating in an emergency state requires immediate corrective action to bring the system back to a secure state without incurring equipment damage.  Until such actions are implemented, the system is at increased risk of loss of reliability.

Figure 1.1 – Operating States of a Power System

While a transmission system is in emergency state, corrective control measures must be taken to avoid equipment damage or system collapse. These steps incur expense of re-dispatching resources or disconnecting various loads, lines, transformers or other equipment. As a result, the SOL violations may be eliminated and the transmission systems recover stability with reconfigured topology, re-dispatched resources, and/or reduced load. Such a state is called a restorative state.  The actions taken may be referred to as re-posturing of the transmission system

1.2 Why State Estimator?

Although Energy Management Systems (EMS) technology has been used to a certain extent for years, utilities were not pressed to utilize tools that demanded highly accurate real-time network models. Instead, operating margins were established to ensure reliability due to the known lack of accuracy of many models and, thus, study results.  This has changed in the energy market environment.  In the new environment, the pattern of flows in the network is less predictable than it is in vertically integrated systems, due to new possibilities associated with open access and the operation of the transmission grid under energy market rules.

Although reliability remains the central issue, the need for accurate real-time network models is also crucial for the proper functioning of energy market related functions. These models are based on the results of the State Estimator.

Based on these network models, operators can detect insecure states related to the power grid reliability and respond with corrective action appropriately.

A functioning State Estimator in a control room is analogous to the headlights of an automobile driving on a dark night, it allows the operator to see hazards ahead and avoid them.

What is a State Estimator?

Network real-time models are built from a combination of snapshots of real-time measurements and static network data. Real time measurements consist of analog values and statuses of switching devices.  Static network data correspond to representative parameters and basic substation configurations. The real-time model is a mathematical representation of the current conditions in a power network as derived from the State Estimator results.

The State Estimator is used to build the real-time network model. Where an adequate redundancy level exists, the State Estimator will eliminate the effect of bad data (erroneous analog measurements) and allow the temporary loss of measurements without significantly affecting the quality of the estimated values. State Estimation is mainly used to filter redundant data, to eliminate incorrect measurements, and to produce reliable state estimates and, to a certain extent, it allows the determination of power flows in parts of the network that are not directly metered. The quality of results obtained from other EMS network and Market Applications depend on the quality of the real-time network model built via state estimation.

In state estimation, network real-time modeling is decomposed into 1) the processing of statuses of switching devices, and 2) the processing of analog data (power flow, power injections voltage magnitude measurements). During topology processing, the status of breakers/switches are processed using a bus-section/switching device network model. During observability analysis and state estimation, the network topology and parameters are treated as given, and analog data are processed using the bus/branch network model. An incorrect network model would be a major source of problems for state estimation process.

Many portions of the area for which a control center is responsible are normally observable. State estimation may be extended to the rest of the network through the addition of pseudo measurements. Pseudo measurements are calculated values presented to the State Estimator as “measurements”, based on load prediction, using the system total demand and load distribution factors.  Use of inaccurate load distribution factors may be another major source of inaccuracies in the state estimation process.

At ERCOT, state estimation is performed every five minute to support both reliability and market applications needs.

Factors Affecting State Estimator Solution Availability and Accuracy

For reasons stated above, the State Estimator must be highly available and provide a solution accurate enough to support the purposes for which it is intended. These do not always happen for several reasons including the following:

- Incorrect  Network Topology

In state estimation, the network toplogy is treated as given and correct. In the event that the topology is incorrect, the state estimator may not converge, or yield grossly incorrect results. The error in topology may stem from 1) inaccurate statuses of breakers and switching device or 2) error in the primitive network model. Inaccuracies in the statuses of switching devices may be caused by temporary or permanent loss of telemetry.

- Inadequate observability

State estimation is extended to the unobservable parts of the network through the addition of pseudo measurements. The pseudo measurements are computed based on load prediction, using load distribution factors. The accuracy of these distribution factors may be questionable when not updated regularly to reflect current conditions. In performing state estimation for the unobservable part of the network, it is possible to corrupt the states estimated from telemetry data

- Inadequate redundancy

Redundant measurements are crucial for the detection and identification of bad data. Higher redundancy ensures better reliability of the state estimator solution in the face of temporary loss of measurements.

- Incorrect Load distribution factors for unobservable parts of the Network

State Estimator Solution Quality Metrics

The assessment of the current state of the network and the accuracy of security analysis and market functions depends highly on the quality of the state estimator solution. The quality of a SE solution is typically measured using one or more of the following indices

- Difference between estimated and telemetry values.(i.e weighted residual)

- Bus MW/MVAR mismatches after SE convergence.

- Convergence rate of SE.

- Measurement visibility of network dynamics

The values of these indices depend upon many factors including:

- Modeling of the electrical devices, connectivity and mapping of telemetries.

- Availability of telemetry and their quality.

- Measurement observability of the network.

- Measurement redundancy of the network. [This term is defined as the ratio of the number of measurements to number of state variables in the observable area of the network.]

- Communication redundancy.

For more detailed information, State Estimator basics, new technologies and maintenance activities are explained in greater depth in Appendix 1

1.3 Why RTCA? (Real Time Contingency Analysis)

Real Time Contingency Analysis (RTCA) as a core function of system security assessment is critical for detecting problems in a large power system and for determining the current security level of the network. A typical RTCA models single element outages (one transmission line or one transformer), multiple-element outages (two lines or 1 generator and one line) and sequential outages (One outage after another). Checking for over limit results is done after each contingency calculation to determine if the transmission system is secure.

The System Operator reviews RTCA results to identify the operating state and to ensure appropriate operating actions are taken.

1.4 Model of ERCOT System

The ERCOT network model is dynamically changing due to forced outages, maintenance activities, and construction or removal of facilities. Table 1 below shows the number of the electrical elements modeled in the network database and how many of them have telemetered measurements or status indications based upon a snapshot collected in March 2004.

| Model Device | Total | Telemetered | % of Telemetered |
| --- | --- | --- | --- |
| Stations | 3536 |  |  |
| Buses | 4730 | 1454 | 30% |
| Lines | 5052 | 2537 | 50% |
| Transformers | 1217 | 431 | 35% |
| Generators | 557 | 557 | 100% |
| Loads | 4572 | 2929 | 64% |
| LTC Taps | 1117 | 256 | 23% |
| Fixed Taps | 100 | 0 | 0% |

Table1.1

In ERCOT’s current model, bus MW/MVar mismatch “around the bus” after SE convergence, is between 15 and 25 MW for 0.5% of buses. The convergence rate is 96% and higher. Measurements are not visible at ERCOT for 11% of buses and 18% of the loads.

1.5 Cost Versus ERCOT Responsibility

The Public Utility Commission of Texas, in Substantive Rule 25.200, assigns to ERCOT the responsibility to “During any period when ERCOT determines that a transmission constraint exists on the transmission system, and such constraint may impair the reliability of a Transmission Service Provider's (TSP's) system or adversely affect the operations of either a TSP or a transmission service customer, ERCOT will take actions, consistent with good utility practice and the ERCOT protocols, that are reasonably necessary to maintain the reliability of the TSP's system and avoid interruption of service.  ERCOT shall notify affected TSPs and transmission service customers of the actions being taken.  In these circumstances, TSPs and transmission service customers shall take such action as ERCOT directs.”   In this rule, transmission is defined as facility (ies) operated at 60 kV or above.

With this responsibility, ERCOT is obligated to determine if a transmission constraint exists on any line 60 kV or above.

To fulfill this obligation, ERCOT must be able to observe, through measurement or calculation, the loading of ERCOT transmission facilities.  Absent observability, ERCOT must confirm through analysis that the unobservable facilities will not be damaged, and calculations performed without the observability will not result in damage to other facilities.

Prudence dictates that ERCOT perform this service at a minimum reasonable cost

2. Observability Analysis – How & Results

A central requirement of monitoring a transmission network is to have sufficient measurements to calculate voltage and angle at each bus.  Without this minimum requirement, system operators cannot know what the real-time flows and expected post-contingency flows are on the transmission system.  Observability defines the percentage of the network meeting this minimum requirement.

To calculate observability, ERCOT personnel have analyzed interconnectivity information of these buses. We found that there are many isolated clusters of interconnected unobservable buses.  We refer to these clusters as unobservable islands. Using the ERCOT data dictionary, we have identified unobservable islands as shown in Appendix 3.

This analysis found that, typically, 11 % of the ERCOT modeled buses are unobservable. Table 2.1 shows the number of unobservable buses at different voltage levels. Table 2.2 shows the number of unobservable islands and their sizes. Table 2.3 below shows total number of buses of each transmission company and how much they are contributing toward the unobservability

| No. | Voltage Level | % of unobservable buses |
| --- | --- | --- |
| 1 | 345 | 0 % |
| 2 | 138 | 2% (100 Buses) |
| 3 | 69 | 9 % (450 Buses) |

Table 2.1

| No. | Unobservable island size | No of Islands |
| --- | --- | --- |
| 1 | 115 | 1 |
| 2 | 22 | 1 |
| 3 | 17 | 1 |
| 4 | 14 | 1 |
| 5 | 12 | 2 |
| 6 | 11 | 1 |
| 7 | 10 | 2 |
| 8 | 9 | 2 |
| 9 | 7 | 1 |
| 10 | 6 | 3 |
| 11 | 5 | 7 |
| 12 | 4 | 7 |
| 13 | 3 | 23 |

Total   = 118.

Table 2.2

| No. | Company | Total No. of Buses | Unobservable Buses | % Unobservability |
| --- | --- | --- | --- | --- |
| 1 | AEP | 887 | 164 | 18.5 |
| 2 | STEC | 172 | 106 | 61.6 |
| 3 | ONCOR | 1819 | 88 | 4.8 |
| 4 | TNMP | 167 | 45 | 30.0 |
| 5 | LCRA | 358 | 30 | 8.4 |
| 6 | BEPC | 342 | 19 | 5.6 |
| 7 | RCEC | 28 | 15 | 53.6 |
| 8 | CNP | 743 | 11 | 1.5 |
| 9 | GEUS | 12 | 7 | 58.3 |
| 10 | PUB | 20 | 5 | 25.0 |
| 11 | DENTON | 14 | 4 | 28.6 |
| 12 | RGEC | 2 | 2 | 100.0 |
| 13 | BRYN | 30 | 2 | 6.7 |
| 14 | TEXLA | 3 | 1 | 33.33 |
| 15 | AEN | 81 | 1 | 1.2 |
| 16 | COGRLD | 19 | 1 | 5.2 |
| 17 | GPL | 19 | 0 | 0 |
| 18 | TMPA | 16 | 0 | 0 |

Table 2.3

A detailed analysis was performed to propose locations of new RTUs to make the ERCOT network fully observable. The process of determining locations of new RTUs and detailed results are provided in Appendix 2 (Observability and RTU placement) and Appendix 3 (RTU Placement Results).

3. Redundancy and Critical Measurements

Measurement redundancy is a key factor in achieving a successful State Estimator implementation. Overall network measurement redundancy is defined as the ratio of total number of analog measurements contributing to observability to the number of state variables. The variables contributing to observability are mainly the branch active and reactive flows and bus active and reactive power injections. Measurement redundancy increases the resilience of the State Estimator. This means that bad or lost telemetry will not result in a solution error in a state estimator with resilience. Obviously this is not an issue if all telemetry is always correct; however, ERCOT has observed telemetry errors/failures very often. In the absence of redundancy, a state estimator cannot filter out bad measurements.  Without redundancy, presence of bad measurements as input will result in an erroneous state estimate, and incorrect flow expectations.

Even though certain networks have large overall measurement redundancy, estimation is very poor in some portions of the network. This happens because redundancy is not uniformly distributed throughout the network. This problem introduces the concept of bus redundancy level.

Based on availability of measurements around a bus, individual bus redundancy level can be evaluated in areas where local redundancy is very poor. Sometimes a single or a group of measurements together makes a bus observable. These measurements are called critical measurements or essential measurements. The more critical measurements in a network; the more vulnerable the system is to an incorrect solution. If one critical measurement is lost, the associated bus becomes unobservable. If one critical measurement is erroneous, it will result in incorrect state and incorrect estimated flows.

ERCOT network measurement redundancy is calculated to be around 1.8. The number of critical measurements in the network is roughly 600.

4. Topology, Validity and Availability

A conventional state estimator uses switch status input data to construct network topology. It assumes that available switch telemetries are correct and, hence, the topology is correct. It then performs the main estimation process, whose primary sub-function is bad data analysis to detect, identify, and rectify any gross measurement errors.  In the absence of good telemetry, SE uses last good value for the topology formation. When the last acquired status is wrong but has a good quality code, SE will use an incorrect topology in its analysis.  If no telemetry is available, SE uses normal status for the non-telemetered switches. Planned outages in an un-telemetered area will not be detected by State Estimator as currently implemented at ERCOT.

Ercot

TO C/C1

TO C/C2

TO C/C3

RTUS

ICCP links

RTU links

ICCP1

FEP

Fig  4. 1

Figure 4.1 above shows how data is being acquired by ERCOT. Data is being acquired by Transmission Operator (TO) control centers from Remote Terminal Units (RTUs). This data is sent to the ERCOT control center via Inter-control Center Communications Protocol (ICCP). As shown above (label ICCP1), there are cases in which there is an ICCP between TO control centers, in which one of the two TO centers is communicating with ERCOT. In this case, if the ICCP1 link breaks, ERCOT loses all data from control center CC1. Some links in ERCOT provide communications redundancy to compensate for such breakdowns, however, most do not.   In the example shown, ERCOT loses data from all RTUs communicating with CC1, even if the ICCP link from ERCOT to that Transmission Operator is available.  This failure mechanism appears when a RTU to TO Control Center communications link fails, but the processing in the TO control center does not make this failure visible to ERCOT.

5. Observability Requirement and Available Exceptions

ERCOT must protect transmission equipment from damage, for any equipment operated at 60 kV or above.  To do this, ERCOT will request RTU placement, at as few locations as practicable.

Prior to requesting additional RTU installation, ERCOT will identify proposed RTU placement(s), the buses which will be made observable by this RTU placement and the relevant post-contingency overloads or under/over voltage conditions.  Upon receipt of this proposed RTU placement, a TSP has 60 days to either:

:

- Provide a proposed alternative to ERCOT for implementation within the next 18 months which meets the requirements described by ERCOT.

- Propose a normal topology change (change normal status of switch(es)) in the area which eliminates the security violations which are ERCOT’s concern. (i.e. eliminates the possibility of flow through a networked element and turns the security problem into a planning problem un-effected by unit dispatch) or

- Address the Public Utility Commission requirement that ERCOT is responsible for the transmission elements designated by ERCOT to be at risk.

In the event that option 3 is selected; ERCOT will immediately remove the elements from its Real Time Congestion Management system as monitored elements pending the resultant PUCT decision.

## 6. Redundancy Standard and Exceptions

ERCOT will maintain redundancy on measurements critical to transmission reliability of the ERCOT interconnection.

ERCOT will identify critical measurements in the ERCOT system.  ERCOT will examine this list of critical measurements and identify those measurements whose loss will result in either:

- Inability of ERCOT to monitor a loading on a transmission element operated at 345 kV or above.

- Inability of ERCOT to monitor loading on a 345/138 kV autotransformer.

- Inability of ERCOT to monitor a loading on a transmission element designated as critical by ERCOT.

ERCOT will also identify critical measurements with:

- A historic availability of less than 80% over any two historic months. (incorrect measurements are considered unavailable in this definition)

ERCOT will request addition of additional measurements, possibly through an independent communications path (if required due to communications failures contributing to item D above) to make these measurement non-critical.  In this request, ERCOT will identify the critical measurement identified, the monitored element of concern, a contingency/overload condition, and a unit dispatch which makes this loading a possible concern.

Upon receipt of a redundant measurement request, a TDSP has 60 days to either:

- Provide ERCOT with a schedule of equipment installations within the next 18 months which will provide the proposed measurement,

- Propose an alternative measurement which will serve the same purpose as the ERCOT identified measurements with a proposed implementation within 18 months,

- Implement corrections to increase the availability rate of the identified critical measurements to an acceptable level, if the request is for reason “D” above; and request from ERCOT permission to defer the proposed additional measurement pending successful availability improvement, or

- Identify and propose a schedule of equipment installations within the next 18 months, which would, as a result, make the transmission element identified by ERCOT non-critical.

Appendix 1

1. State Estimator Basics

The real-time modeling of power network follows a five-step procedure involving:

- Network topology processing

- Measurement consistency processing

- Observability Analysis

- State Estimation

- Bad data processing

Steps 1, 2 and 3 assume that switching device statuses are correct. Step 4 additionally assumes that the network parameters (branch impedances and line charging) are correct. Step 5 processes bad data assuming they are caused by analog measurements only.

1.1 Network Topology processing (NTP)

NTP collects telemetered statuses of breakers and switches. The SCADA quality codes are checked. The last acquired good statuses are used for switches with bad quality code. Database-entered normal status is used for any switching device with no telemetered status.

The NTP transforms the bus-section/switching-device model into the more compact bus/branch model, identifies energized electrical islands and removes de-energized and grounded equipment from the model.

During observabilty analysis and state estimation, the network topology as described by the bus/branch model and parameters are considered as given. Analog data are processed using the bus/branch network model. In the event that the topology is wrong, as may happen when wrong telemetered switch statuses (with good quality code) are received or when the normal status of an un-telemered switch is different from the current status, the State Estimator may not solve or, if it solves, give wrong results.

1.2 Measurements Consistency Checking

The measurement set is first checked for consistency. This procedure filters out voltage measurements that are outside of 70% and 130% of nominal values; flows in open-ended equipment; in-service branches with flows below a set tolerance; etc

1.3 Observability Analysis

If there enough telemetered measurements and they are well distributed throughout the network in such a way that the state estimation is possible, the network is said to be observable.  If a network is not observable, it is still useful to know which portions have a state which can be estimated, i.e., it is important to determine the observable islands. In the observable parts of the network, measurement redundancy is defined as the ratio of the number of measurements to the number of states. In most practical cases the redundancy in the range 2.5 – 2.8. A critical measurement is a non-redundant measurement, i.e., a measurement that when removed turns the network unobservable.

Network observability determines which variables, and the equations used to solve for them, will constitute the state estimation problem formulation. In other words the observability function determines what variables are solvable with the available network information. This is done for the current network bus structure and available measurement set. The availability of usable measurement and model injection information determines which equations can be used. In general, there will be more equations than variables, but if n variables are to be determined, then there must be at least n equations that are independent in these variables. The term "observable" itself applies directly to variables. A set of variables is observable if it can be determined from a given set of equations and available measurement data. A distinction should be made between the terms "observable", which basically means solvable or non-singular, and "measurement observable", which means that the variables are solvable from measured input or observations. For a given set of switching device positions, the network can be divided into more than one island, where an island is a set of buses connected by closed branches. Similarly, for a given set of usable equations, the network may be divided into more than one observability island. An observable island is a group of buses whose voltage magnitudes and relative phase angles can be determined from these equations. The determination of the extent of measurement observability itself is based directly upon Kirchoff's laws. Its core is the application of two simple rules:

1. A branch flow is known if the buses at each end are in the same observability island. i.e. their state (voltage and angle) can be calculated from available measurements and network equations.

2. If all unknown branches incident to an available measured injection bus terminate in observability Island, then the injection bus is also in that observability Island. An available measured injection bus is one for which all injections are measured. (This includes zero injection buses).

In addition, there must be at least one known voltage magnitude in an observability island in order for it to be observable. Measurements are used in strict preference to model injection information in the observability determination. First, measurements are used to make as much of the network observable as is possible. This involves the application of the two rules listed above to determine the extent of measurement observability. The results of this stage determine the extent to which the time schedule model can be updated from measurement information. Next, available model injection information is used, only as needed, to complete the observability of the network. This means that for all of the desired solution variables that are not solvable from equations using SCADA data, additional equations are inserted which will incorporate model injection information, or "pseudo-measurements". In the ERCOT model, the only types of pseudo-measurements used are unit and load injections. The only type of equations used for this final extension is bus constraint equations (i.e. sum of bus is zero). Thus, outside of the measurement observable portions of the model, the State Estimator problem formulation is like a load flow with one equation per unknown.

If a bus and all the buses directly connected to it are measurement observable, then the injection is observable at that bus. It means if there is any load at that bus, it can be estimated and can also be adapted. In event of temporary loss of telemetry on this bus, this adapted load value can be used as an input and it gives out accurate SE results. In the unobservable portion of the network, SE runs based on the load schedules which are not adapted. This portion of the network is very susceptible to security problems. The estimation results and contingency assessment is this area is always questionable since we have non-adapted loads, insufficient breaker and disconnect status information and lack of real time analog flow, tap and voltage measurements. Fundamentally it is equivalent to running load flow in the unobservable area with constant load rather than state estimation. This makes contingency assessment in these areas questionable. Real contingency overloads may go unnoticed and constraints may be invoked and re-dispatched unnecessarily.  This effect will clearly affect nodal prices if implemented in ERCOT.

1.4 WLS State Estimator

The State Estimator problem is formulated as over-determined systems of non-linear equations solved as a Weighted Least Squares problem.

Problem Formulation

Considering the nonlinear measurement model:

zj=hj(x)+ej

Where,

zj is the jth measurement

x is the true state vector

hj(.) is a non-linear scalar function relating the jth measurement to states, and

ej is the measurement error which is assumed to have zero mean and variance

σj

There are m measurements and nstate variables, n<m

The WLS state estimator is formulated mathematically as an optimization problem with quadratic objective function and with equality and inequality constraints.

Minimize J(x)=12rj2σj2

Subject to gi(x)=0		i=1,ng

ci(x)≤0		i=1,nC

Where rj is the residual zj−hj(x), J(x)is the objective function

gi(.) and ci(.) are functions representing power flow quantities.

Equality and inequality constraints are used to represent target values and operating limits in the unobservable parts of the network.

State Variables

The vector of state variables includes the following:

- Nodal voltage

  - Voltage magnitude Vk

  - Voltage angle θk

- LTC transformer tap, tkm

Analog Measurements

The following analog measurements are included in the state estimator:

- Voltage magnitude

- Active power

  - Branch flow

  - Bus injection

- Reactive power

  - Branch flow

  - Bus injection

- Current magnitude flow

- LTC tap

- Active power flow

  - In switches

  - In zero impedance branches

- Reactive power flow

  - In switches

  - In zero impedance branches

Equality Constraints

Target values normally used in power flow studies are included in the state estimator in order to restore observability to those parts of the network that are permanently or temporarily unobservable. These include:

- Target or specified voltage magnitude

- Zero injection bus

Equality constraints are treated as pseudo-measurements with relatively high weights. As such, a numerically robust solution method is used to solve the estimation problem.

Inequality Constraints

Limits, such as minimum and maximum reactive power generation, are also used to improve representation of unobservable parts of the network. These are:

- Generator VAR limits

- LTC tap limits

Inequality constraints are dealt with the same way as in power flow calculations. The constraints are initially relaxed, as one approaches the solution those constraints that are violated are enforced on the corresponding limits as pseudo-measurements with relatively high weights.

Solution by Orthogonal Transformation Method

The need to represent equality constraints as pseudo measurements with relatively high weights has necessitated the use of the orthogonal transformation algorithm to solve the estimation problem.

When a solution is obtained, the cost J is compared to a given validity threshold. This threshold is set so that if all of the errors are within their expected ranges, as defined by the uncertainty models, then J will be less than the threshold and the solution is considered to be valid. However, if it is greater than this threshold, then an error analysis is performed that typically results in some weights being adjusted to reflect unexpected errors that are detected, such as an anomalous measurement. The network solution is then updated to reflect the weight changes, and the total cost J is again compared against the validity threshold, and so on until a valid solution is obtained.

1.5 Bad Data Detection and Filtering

Each equation in the state estimator problem formulation is considered to be uncertain, i.e., the relationship between variables, measurements and parameters expressed by each of these equations is considered to be inexact. Measurement random error components and imperfect knowledge of component electrical models, e.g., impedances, are some of the sources of this uncertainty. Such uncertainty is represented in RTNET with uncertainty models. Uncertainty models are defined through assigned accuracy classes, defined in the modeling application. Every analog measurement which RTNET uses as input from SCADA and each type of modeled input information, or pseudo-measurement, is assigned to an accuracy class. An accuracy class provides a means for the user to specify the expected error in a piece of RTNET input information that is assigned to that accuracy class. The final form of the expected error is a standard deviation value which RTNET in turn uses to calculate an equation weight. The weight for measurement equations is determined from the single measurement standard deviation associated with the equation. The weight for bus equations is determined from the sum of standard deviations associated with the bus injections and the basic Kirchoff's current law uncertainty standard deviation. For a given accuracy class the user can either specify equipment error components that will be summed to determine a per-unit value of standard deviation, directly specify the standard deviation, or specify equipment error components plus a bias to derive a standard deviation. In each case the per-unit value of standard deviation derived from an accuracy class will be scaled by a base value to convert it to a standard deviation in engineering units. These base values can be specified in the accuracy classes. If a base value is not specified in an accuracy class, RTNET will derive one from the network devices involved in the equations for which the uncertainty models are being developed. Each uncertainty model describes a zero mean error with a specified standard deviation. The error is nominally interpreted as being a Gaussian random variable with these characteristics. The model predicts that over many solutions, if the difference between a particular line flow's measured and calculated MW values was examined, the mean error would be zero and the standard deviation of the errors would be specified by the measurement's uncertainty model.

If we formed a histogram of these errors and the familiar bell-shaped normal distribution curve emerged, then the gaussian interpretation would be supported. If actual errors behave in accordance with this model, then they will almost always be within a few standard deviations of zero. Errors that are consistently outside of this range mean that something is wrong with the uncertainty model. Each uncertainty model includes another parameter, called the breakpoint, which is specified in the associated accuracy class and which defines this range of reasonability for the gaussian model. Errors outside of this range are considered to be completely unknown, i.e., they are considered to be unpredictable in a probabilistic sense. For each equation, the breakpoint is an important parameter that is used in the error analysis logic of RTNET for identifying anomalies, etc. At a network solution, equations whose weighted residual errors are outside of their breakpoints are always suspect, and the process of obtaining a valid solution focuses only on suspect equations. Breakpoints are also specified in the accuracy class data structure. The main point of this discussion on error modeling is the practical result that a weight is calculated for each equation. This weight is a measure of the level of confidence that is assigned to a measurement. It is a positive real number that is inversely proportional to the equation uncertainty, which is represented by the equation's standard deviation. Specifically, the nominal weight of the kth measurement is:

Wk=1σ2                                                                                               (10)

i.e., the inverse of the equation variance.

A short summary of the error processing mechanism is as follows. To detect a measurement with error, the state estimator compares the weighted residual of each equation with the equation's break point, supplied as part of the uncertainty model for that equation. If the weighted residual is greater than the break point, it is considered to have greater than the expected amount of error. This equation is called "suspect". For each equation that is suspect, the weight of the equation is reduced by the error analysis logic in order to obtain a valid solution. Each equation has a weight multiplier used for this purpose. Equation weight multipliers are less than 1.0 when an equation is "deweighted". As a weight multiplier approaches zero, the equation's effect on the solution becomes less and less, until at zero its effect is exactly as if it did not exist at all. An equation with a zero multiplier is called "anomalous".

2. Topology Estimator

A conventional state estimator uses switch status input data to construct network topology. It then performs the main estimation process, whose primary sub-function is bad data analysis to detect, identify, and rectify any gross measurement errors. Unfortunately, conventional bad data analysis algorithms are fundamentally designed to find only analog measurement errors, on the assumption that the network topology is correct. When this assumption is false, which happens very often in practical large power system network, these algorithms typically malfunction and produce either no state estimate or an estimated model with an incorrect and potentially dangerous topology. It makes the results of security assessment functions and market functions largely erroneous.

Although there have been some inroads in the industry to develop a form of topology error detection within the state estimation formulation, these methods have not been found to be accurate under a number of conditions including the presence of multiple interacting bad data. It has been recognized later that the combinatorial approach is the most powerful methodology for state estimation bad data analysis. This approach involves a systematic search of hypothesized combinations of bad measurements and is particularly effective for data including switch status errors. For each such combination, the supposed bad data is corrected or removed and resulting state estimator solution is tested for accuracy. At the end, the case registering the highest accuracy represents the most plausible bad data combination.

Topology errors have been noticed in the ERCOT state estimator very often due to wrong switching device telemetries and it makes the daily Operations very uncomfortable. Hence ERCOT is moving towards implementation of Topology estimation techniques in the Operations environment.

3. Time Schedule Model Implementations

Based on the availability of telemetries, a large power system network can be categorized into two regions namely observable regions and unobservable regions. There may be multiple numbers of unobservable regions scattered here and there in a large network. In the observable regions of the network, the bus injections are observable and hence loads are estimated. These estimated loads are adapted. Whenever observable portions of a network becomes unobservable due to temporary loss of telemetries, these adapted load values are used as the input to run the estimation in that portion of the network and it gives reasonably good solution.

In the permanent unobservable pockets of the network, the primitive load schedules are used as the input to the state estimation to evaluate the state and hence the flows. It means unlike in the observable areas, loads are not estimated and not adapted in the unobservable areas. In other words state estimation basically performs load flow in the unobservable areas using primitive load schedules.  The accuracy of the results in the unobservable area basically depends how accurate and realistic is the primitive load model with respect to time, weather and season.  In many implementations, there have been a lot of attempts to granulate load schedules in the unobservable areas with respect time and season. But it has been observed it is not successful since there has been always some error in the data collected and periodic load survey has not been possible due to lack of man power, time and technical difficulties. In ERCOT model, loads in the unobservable areas are modeled as invariant with respect to time and season and it makes the state estimation results in these areas questionable. And the error in this load model affects all offline studies like outage scheduling studies, RMR studies etc.

4. Manual Interventions in the state estimator

It is the responsibility of Operations Engineers to make real time sequence (SE /RTCA) available to Operators 24/7 basis with best possible solution irrespective of real time dynamics in the telemetries and periodic model changes.  They keep an eye on bus mismatches, measurement residuals, base case overloads, RTCA results, OAG link status, and anomalous measurement data, real time sequence messages etc. The abnormalities in the items aforesaid lead to investigations to find out the cause. They find various reasons like modeling issues like wrong impedances, wrong telemetry mapping, wrong model layout, wrong ratings etc. They observe various telemetry issues like telemetry swapping, wrong analog and status telemetry, loss of telemetries, loss of ICCP link, wrong quality code etc.  To resolve them they do the following.

- Update the ratings in the real time model as soon as they get service request from the TDSPs temporarily and make sure they get in the database in the forthcoming DB load.

- Check with TDSP about the rating information currently existing in the ERCOT model, if they seem to be questionable.

- Report Modeling issues to modeling group and coordinate with TDSP and modeling group to get them corrected in the database.

- Report telemetry mapping issues to modeling group and ICCP/telemetry personnel to get them corrected

- Report wrong telemetries , lack of telemetries and ICCP outages to ICCP/Telemetry personnel and get them corrected

- Manually override tap information to make reactive power balance at level if the taps are not measured or measured with wrong value.

- Manually override generations if they are not measured, but found to be feeding the ERCOT grid.

- Manually change status of switching devices if they found to be wrong.

- Disable wrong analog telemetries.

- Change the accuracy class of telemetries, they belong to.

- Involve in the periodic DB load and make sure real time sequence is perfect after DB load.

- Change the state estimation process parameters like tolerance, damping factors, cold start flag etc on need basis.

Sometimes Operations Engineers have to fudge the data like transformer tap, switching device status and generations to make SE functional if they are not measured. This would resolve the problem with SE temporarily, but it is going to be dangerous in a long run since we are not getting time variant values either through telemetries or service requests. It seems to be difficult to keep track of these manual entries and it contaminates the model and in turn the real time results in the long run.

Appendix 2

Observability and RTU placement

From the section 2, it is apparent that how much of ERCOT network is observable. To make these buses and loads observable we need to install new RTUs at some of the stations. To make the investment less, it is essential to find out locations to put up RTUs. The stations having large number of unobservable buses connected are the optimal locations. Each unobservable island has to be analyzed individually to find out optimal locations. The following heuristic algorithm describes how to find new RTU locations.

- Form a binary matrix based on the connectivity of the Unobservable buses in an island.

- Store the SL/G index of all Unobservable Stations, SL/GI (Station Load/Generator Index) means number of Loads/Generators connected to an unobservable station.

- Find out the Station Connectivity Index (SCI) – SCI means number of Unobservable Buses connected to the station.

- Assign a feasibility flag to every station. If it is not possible to install RTU at a station due to lack of communication infrastructure or any other reason, we make that station infeasible.

- Select the station having highest SCI to have RTU. If there are more than one, take the one having highest SL/GI to place RTU.

- Make all elements of the columns having 1 in the row of the selected location to 0.

- Check for 0 injection measurement observability. If any bus is observable by the help of the new RTU and 0 injections/known injections, make all the 1’s in the corresponding columns to 0.

- Recalculate SCI and repeat above 3 steps till SCI for all stations becomes 0.

It has to be noted at least one RTU has to be placed either at one boundary bus or at any unobservable bus directly connected to an unobservable bus in an island so that every unobservable island becomes part of the large observable island through RTU placements.

The above algorithm can be explained with help of an example with shown in the Fig 1 below.

gjjhhjhjhjhjhj

FTLN.T

MESAV_SW.B(16)

SHEF.B(15)

IRAN.U(2)

MART.U(1)

MDSC.U(3)

AIRP.U(5)

ARPT.U(4)

YATW_SW.U(6,7)

WESTYA.U(8)

MESAVIEW.U(9)

INDNENR.U(11)

INDNENR.U(10)

INDNNWP.U(12)

INDN.U(13)

RIOP.T

MCAM.U(14)

MCAN_SW.T

Fig  1.

In the single line diagram shown in Fig 1 above, red lines are 69Kv and blue lines are 138Kv. All the buses with .T extension are the telemetered ones, the ones with .B extension are the boundary buses and the one with .U extension are the unobservable buses. There are 14 unobservable buses, 7 unobservable loads, 3 unobservable generator buses, 6 unobservable 69Kv lines, 10 unobservable 138Kv lines and one 69/138 unobservable transformer. In this assume that all stations are feasible to have an RTU. Form a binary matrix as below using the algorithm described above. The head row numbers 1,2…14 are the bus numbers, and column numbers 1,2 … 14 are the station numbers. Since buses 6 and 7 belong to same station, station is numbered as 6, 7. SCI of each row is calculated by adding all the 1’s in the corresponding row.

1       2      3     4    5     6     7     8    9   10    11   12    13    14    SCI   SL/GI

1       1       1      1     1    0     0     0     0    0     0     0     0      0      0      4       1

2       1       1      0     0    0     0     0    0     0     0     0     0      0      0      2       1

3       1       0      1     0    0     0     0    0     0     0     0     0      0      0      2       1

4       1       0      0     1    1     1     0    0     0     0     0     0      0      0      4       0

5       0       0      0     1    1     0     0    0     0     0     0     0      0      0      2       1

6,7       0       0      0     1    0     1     1    1     0     0     0     0      0      0      4       0

8       0       0      0     0    0     0     1    1     1     1     0     0      0      0      4       0

9       0       0      0     0    0     0     0    1     1     0     0     0      0      0      2       1

10,11       0       0      0     0    0     0     0    1     0     1     1     1      0      1      5       2

12       0       0      0     0    0     0     0    0     0     0     1     1      1      0      3       1

13       0       0      0     0    0     0     0    0     0     0     0     1      1      0      2       1

14       0       0      0     0    0     0     0    0     0     1     0     0      0      1      2       1

For the matrix shown above 10,11 is the station having highest SCI. So this is the station to have first RTU.RTU at (10,11) makes buses 10,11,12,14 and 8 Observable. Also since we know Generator telemetries at 12, bus 13 also becomes observable. Now nullify all the 1’s in the columns of new observable buses and build the new binary matrix which is shown below.

1      2     3    4     5      6     7     8    9   10    11   12    13    14    SCI   SL/GI

1      1      1     1    1     0      0     0     0    0    0      0     0      0       0      4       1

2      1      1     0    0     0      0     0     0    0    0      0     0      0       0      2       1

3      1      0     1    0     0      0     0     0    0    0      0     0      0       0      2       1

4      1      0     0    1     1      1     0     0    0    0      0     0      0       0      4       0

5      0      0     0    1     1      0     0     0    0    0      0     0      0       0      2

6,7      0      0     0    1     0      1     1     0    0    0      0     0      0       0      3       0

8      0      0     0    0     0      0     1     0    1    0      0     0      0       0      2       0

9      0      0     0    0     0      0     0     0    1    0      0     0      0       0      1       1

10,11      0      0     0    0     0      0     0     0    0    0      0     0      0       0      0       2

12      0      0     0    0     0      0     0     0    0    0      0     0      0       0      0       1

13      0      0     0    0     0      0     0     0    0    0      0     0      0       0      0       1

14      0      0     0    0     0      0     0     0    0    0      0     0      0       0      0       1

For the matrix shown above, 1 is the station having highest SCI. So this is the station to have second RTU. RTU at station 1, makes buses 1, 2, 3 and 4 Observable. Now nullify all the 1’s in the columns of new observable buses and build the new binary matrix which is shown below.

1      2     3    4     5      6     7     8    9   10    11   12    13    14    SCI   SL/GI

1       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0        1

2       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0        1

3       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0        1

4       0      0     0    0     1      1     0     0    0    0      0     0      0      0      2        0

5       0      0     0    0     1      0     0     0    0    0      0     0      0      0      1        1

6,7       0      0     0    0     0      1     1     0    0    0      0     0      0      0      2        0

8       0      0     0    0     0      0     1     0    1    0      0     0      0      0      2        0

9       0      0     0    0     0      0     0     0    1    0      0     0      0      0      1        1

10,11       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0        2

12       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0        1

13       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0        1

14       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0        1

For the matrix shown above, all stations are having equal RTU placement priority. The station 6,7 is selected to put up third RTU. It makes the buses 6 and 7 observable. Also it makes buses 5 and 9 observable using available measurements and 0 injections. Now nullify all the 1’s in the columns of new observable buses and build the new binary matrix which is shown below.

1      2     3    4     5      6     7     8    9   10    11   12    13    14    SCI   SL/GI

1       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0       1

2       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0       1

3       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0       1

4       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0       0

5       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0       1

6,7       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0       0

8       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0       0

9       0      0     0    0     0      0     0     0    0    0      0     0      0      0      0       1

10,11      0      0     0    0     0      0     0     0    0    0      0     0      0      0      0       2

12      0      0     0    0     0      0     0     0    0    0      0     0      0      0      0       1

13      0      0     0    0     0      0     0     0    0    0      0     0      0      0      0       1

14      0      0     0    0     0      0     0     0    0    0      0     0      0      0      0       1

SCI is zero for all stations. So the network is observable with three additional RTUs.

The fully observable network is shown in Fig 2 below with new RTUs.

FTLN.T

MESAV_SW.B(16)

SHEF.B(15)

IRAN.U(2)

MART.U(1)

MDSC.U(3)

AIRP.U(5)

ARPT.U(4)

YATW_SW.U(6,7)

WESTYA.U(8)

MESAVIEW.U(9)

INDNENR.U(11)

INDNENR.U(10)

INDNNWP.U(12)

INDN.U(13)

RIOP.T

MCAM.U(14)

MCAN_SW.T

Fig 2

Appendix 3

RTU placement Results

A detailed analysis is done for all unobservable islands in the ERCOT network based on the modeled data on ERCOT system as of March’ 2004 using the heuristic methodology described in the Appendix 1 and its results are tabulated below. Individual column titles are defined as

NumUBus : Number of unobservable buses in an island.

Islandnum : It is island number.

Fcomp : The name of the company to which the station belongs to.

Fstatus : The observability status of the station. ‘U’means the bus is unobservable and ‘b’ means it is observable boundary bus.

Fstn : The station mnemonics of the bus it belongs to.

Stnname: The name of the station.

FBLI : It is the bus load index. The number of loads connected to a bus.

RTUpref : The preference of the RTU. The lower is the number, higher is the priority. It this box is null, it means RTU is not needed there.

N : The number of buses which can be made observable by installing preferred RTU at a station.

| b means boundary bus, U means Unobservable bus, FBLI( Bus load index) means number of loads connected to a bus. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| NumUBus | Islandnum | Fcomp |  |  |  |  |  |  | Fstatus |  |  |  |  |  |  |  | Fkv |  |  | Fstn |  |  |  |  |  | stnname |  |  |  |  |  |  |  | FBLI |  |  |  | RTUpref |  |  |  |  |  |  |  |  |  | N |  |
| 114 | 84 | AEP |  |  |  |  |  |  | b |  |  |  |  |  |  |  | 69 |  |  | DEVINE |  |  |  |  |  | DEVINE |  |  |  |  |  |  |  | 2 |  |  |  | 17 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MARKHAM |  |  |  |  |  | MARKHAM |  |  |  |  |  |  |  | 1 |  |  |  | 21 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MATHIS |  |  |  |  |  | MATHIS |  |  |  |  |  |  |  | 2 |  |  |  | 7 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PALACIOS |  |  |  |  |  | PALACIOS |  |  |  |  |  |  |  | 2 |  |  |  | 34 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ROBSTWN |  |  |  |  |  | ROBSTOWN CITY |  |  |  |  |  |  |  | 0 |  |  |  | 27 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SAN_DIEG |  |  |  |  |  | SAN DIEGO |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SMITH |  |  |  |  |  | SMITH |  |  |  |  |  |  |  | 2 |  |  |  | 33 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 69 |  |  | BYCTYPM1 |  |  |  |  |  | BAY CITY PUMP 1 |  |  |  |  |  |  |  | 1 |  |  |  | 47 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BYCTYPM3 |  |  |  |  |  | BAY CITY PUMP 3 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CSABLK |  |  |  |  |  | CASA BLANCA |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | EDROY |  |  |  |  |  | EDROY |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LYTLE2 |  |  |  |  |  | LYTLE CSW |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ROB_CPL |  |  |  |  |  | ROBSTOWN |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | STEVENS |  |  |  |  |  | STEVENS |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | LCRA |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 69 |  |  | FRDTRN |  |  |  |  |  | FORDTRAN |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WESSER |  |  |  |  |  | WESER |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | STEC |  |  |  |  |  |  | b |  |  |  |  |  |  |  | 69 |  |  | BATESVL |  |  |  |  |  | BATESVILLE SWITCH |  |  |  |  |  |  |  | 0 |  |  |  | 31 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CALALS |  |  |  |  |  | CALALLEN SUB |  |  |  |  |  |  |  | 1 |  |  |  | 6 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | COTULAS |  |  |  |  |  | COTULLA SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DANEVA |  |  |  |  |  | DANEVANG |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DANEVAS |  |  |  |  |  | DANEVANG DIST SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DILLYSTE |  |  |  |  |  | DILLEY SWITCH STEC |  |  |  |  |  |  |  | 1 |  |  |  | 32 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DOWNIES |  |  |  |  |  | DOWNIE SUB |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ELCMPOS |  |  |  |  |  | EL CAMPO SUB |  |  |  |  |  |  |  | 1 |  |  |  | 23 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FRANKC |  |  |  |  |  | FRANKLINS CAMP |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | GEOWEST |  |  |  |  |  | GEORGE WEST |  |  |  |  |  |  |  | 0 |  |  |  | 5 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HOLANDS |  |  |  |  |  | HOLLAND SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HONDOCS |  |  |  |  |  | HONDO SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ORNGROV |  |  |  |  |  | ORANGE GROVE |  |  |  |  |  |  |  | 0 |  |  |  | 14 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PRTLAVS |  |  |  |  |  | PORT LAVACA SUB |  |  |  |  |  |  |  | 1 |  |  |  | 36 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | RFUGIOS |  |  |  |  |  | REFUGIO SUB |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | RVIERAS |  |  |  |  |  | RIVIERA SUB |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SANMGSW |  |  |  |  |  | SAN MIGUEL 69 KV SWI |  |  |  |  |  |  |  | 0 |  |  |  | 4 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SCHRODS |  |  |  |  |  | SCHROEDER SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | VANBLT |  |  |  |  |  | VANDERBILT SWITCHYAR |  |  |  |  |  |  |  | 0 |  |  |  | 3 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 138 |  |  | BRUNI |  |  |  |  |  | BRUNI SUB |  |  |  |  |  |  |  | 0 |  |  |  | 15 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PEARSALL |  |  |  |  |  | PEARSALL SWITCH |  |  |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  |  |  | 6 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ROSSVLS |  |  |  |  |  | ROSSVILLE |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 69 |  |  | BAYCTYS |  |  |  |  |  | BAY CITY SUB |  |  |  |  |  |  |  | 1 |  |  |  | 8 |  |  |  |  |  |  |  |  |  | 4 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BEEVLES |  |  |  |  |  | BEEVILLE SUB |  |  |  |  |  |  |  | 1 |  |  |  | 46 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BEPRISS |  |  |  |  |  | BEEVILLE PRISON SUB |  |  |  |  |  |  |  | 1 |  |  |  | 28 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BIGFOTS |  |  |  |  |  | BIG FOOT SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BIGWELS |  |  |  |  |  | BIG WELLS SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BONNIES |  |  |  |  |  | BONNIEVIEW SUB |  |  |  |  |  |  |  | 2 |  |  |  | 43 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BRUNDGS |  |  |  |  |  | BRUNDAGE SUB |  |  |  |  |  |  |  | 1 |  |  |  | 29 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BRUNI |  |  |  |  |  | BRUNI SUB |  |  |  |  |  |  |  | 1 |  |  |  | 15 |  |  |  |  |  |  |  |  |  | 2 |  |
| NumUBus | Islandnum | Fcomp |  |  |  |  |  |  | Fstatus |  |  |  |  |  |  |  | Fkv |  |  | Fstn |  |  |  |  |  | stnname |  |  |  |  |  |  |  | FBLI |  |  |  | RTUpref |  |  |  |  |  |  |  |  |  | N |  |
|  |  | STEC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CALHSW |  |  |  |  |  | CALLIHAM SWITCH |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CARANCS |  |  |  |  |  | CARANCAHUA SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CARIZOS |  |  |  |  |  | CARRIZO SPRINGS SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CHARCOS |  |  |  |  |  | CHARCO SUB |  |  |  |  |  |  |  | 2 |  |  |  | 44 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CHARLTS |  |  |  |  |  | CHARLOTTE SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CHKPRIS |  |  |  |  |  | CHOKE CANYON PRISON |  |  |  |  |  |  |  | 1 |  |  |  | 48 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CLEMVSW |  |  |  |  |  | CLEMVILLE SWITCH |  |  |  |  |  |  |  | 0 |  |  |  | 22 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CNTRALS |  |  |  |  |  | CENTRAL SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CORPSSW |  |  |  |  |  | CORPUS CHRISTI SWITC |  |  |  |  |  |  |  | 0 |  |  |  | 37 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CORPUS |  |  |  |  |  | CORPUS CHRISTI SUB |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | COYCTYS |  |  |  |  |  | COY CITY SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CRSTLS |  |  |  |  |  | CRYSTAL CITY SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CRSTLSW |  |  |  |  |  | CRYSTAL CITY 69KV SW |  |  |  |  |  |  |  | 0 |  |  |  | 12 |  |  |  |  |  |  |  |  |  | 4 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DERBYS |  |  |  |  |  | DERBY SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DEVNES |  |  |  |  |  | DEVINE SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DHANIS |  |  |  |  |  | DHANIS SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DILLEYS |  |  |  |  |  | DILLEY SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DRSCOLS |  |  |  |  |  | DRISCOLL SUB |  |  |  |  |  |  |  | 1 |  |  |  | 9 |  |  |  |  |  |  |  |  |  | 4 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | EDNAS |  |  |  |  |  | EDNA SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ELTORS |  |  |  |  |  | EL TORO SUB |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ELTORSS |  |  |  |  |  | EL TORO SWITCHING ST |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ELTORSW |  |  |  |  |  | EL TORO SWITCH |  |  |  |  |  |  |  | 0 |  |  |  | 24 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FASHNGS |  |  |  |  |  | FASHING SUB |  |  |  |  |  |  |  | 1 |  |  |  | 18 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FERRIS |  |  |  |  |  | FERRIS SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FERRISW |  |  |  |  |  | FERRIS SWITCH |  |  |  |  |  |  |  | 0 |  |  |  | 38 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FORTRSW |  |  |  |  |  | FORDTRAN SWITCH |  |  |  |  |  |  |  | 0 |  |  |  | 39 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FREERS |  |  |  |  |  | FREER SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FRIOTOS |  |  |  |  |  | FRIO TOWN SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | GANADOS |  |  |  |  |  | GANADO SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | GANADSW |  |  |  |  |  | GANADO SWITCH |  |  |  |  |  |  |  | 0 |  |  |  | 10 |  |  |  |  |  |  |  |  |  | 4 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | GEOWSTS |  |  |  |  |  | GEORGE WEST DIST SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | GOLIADSW |  |  |  |  |  | GOLIAD SWITCH |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HIGHLAS |  |  |  |  |  | HIGHLANDS SUB |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | INDPK9 |  |  |  |  |  | INDUSTRIAL PARK SUB |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | INDPKSW |  |  |  |  |  | INDUSTRIAL PARK GOAB |  |  |  |  |  |  |  | 0 |  |  |  | 25 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | INEZS |  |  |  |  |  | INEZ SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | KAMEYS |  |  |  |  |  | KAMEY SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | KENEDYS |  |  |  |  |  | KENEDY |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LEONAS |  |  |  |  |  | LEONA SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LOLITAS |  |  |  |  |  | LOLITA SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LONETRS |  |  |  |  |  | LONE TREE |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LOUISES |  |  |  |  |  | LOUISE |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MATHI_ST |  |  |  |  |  | MATHIS SUB |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MOORES |  |  |  |  |  | MOORE SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MRKHMSW |  |  |  |  |  | MARKHAM AIR SWITCH |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NBATSVS |  |  |  |  |  | NORTH BATESVILLE SUB |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NCALHMS |  |  |  |  |  | NORTH CALLIHAM SUB |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NumUBus | Islandnum | Fcomp |  |  |  |  |  |  | Fstatus |  |  |  |  |  |  |  | Fkv |  |  | Fstn |  |  |  |  |  | stnname |  |  |  |  |  |  |  | FBLI |  |  |  | RTUpref |  |  |  |  |  |  |  |  |  | N |  |
|  |  | STEC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NCLMVLS |  |  |  |  |  | NORTH CLEMVILLE SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NURSRYS |  |  |  |  |  | NURSERY SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | OAKS9 |  |  |  |  |  | OAKS SUB |  |  |  |  |  |  |  | 1 |  |  |  | 16 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | OLIVIAS |  |  |  |  |  | OLIVIA SUB |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | OLMOS_S |  |  |  |  |  | OLMOS SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ORNGRVS |  |  |  |  |  | ORANGE GROVE DIST SU |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | OVILASW |  |  |  |  |  | OLIVIA GOAB SWITCH |  |  |  |  |  |  |  | 0 |  |  |  | 13 |  |  |  |  |  |  |  |  |  | 4 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PEARSALL |  |  |  |  |  | PEARSALL SWITCH |  |  |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  |  |  | 6 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PLACIOS |  |  |  |  |  | PALACIOS SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PLANVWS |  |  |  |  |  | PLAINVIEW SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PLCEDOS |  |  |  |  |  | PLACEDO SUB |  |  |  |  |  |  |  | 1 |  |  |  | 19 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PLSNTOS |  |  |  |  |  | PLEASANTON SUB |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PORTOCS |  |  |  |  |  | PORT OCONNOR SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | POTEETS |  |  |  |  |  | POTEET SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | RAYBURN |  |  |  |  |  | SAM RAYBURN SWITCHYD |  |  |  |  |  |  |  | 0 |  |  |  | 2 |  |  |  |  |  |  |  |  |  | 4 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | RBTWNCTY |  |  |  |  |  | CITY OF ROBSTOWN |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | RICRDOS |  |  |  |  |  | RICARDO SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | RMOTTS |  |  |  |  |  | ROUND MOTT SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | RMOTTSW |  |  |  |  |  | ROUND MOTT GOAB SWIT |  |  |  |  |  |  |  | 0 |  |  |  | 40 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ROBSTOS |  |  |  |  |  | ROBSTOWN SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | RVRSDS |  |  |  |  |  | RIVERSIDE SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | S_BATES |  |  |  |  |  | SOUTH BATESVILLE SUB |  |  |  |  |  |  |  | 1 |  |  |  | 35 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | S_CALHS |  |  |  |  |  | SOUTH CALLIHAM SUB |  |  |  |  |  |  |  | 1 |  |  |  | 30 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | S_CLMVS |  |  |  |  |  | SOUTH CLEMVILLE SUB |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SABINLS |  |  |  |  |  | SABINAL SUB |  |  |  |  |  |  |  | 1 |  |  |  | 20 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SANDIAS |  |  |  |  |  | SANDIA SUB |  |  |  |  |  |  |  | 2 |  |  |  | 45 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SARGNTS |  |  |  |  |  | SARGENT SUB |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SIMMONS |  |  |  |  |  | SIMMONS SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SNDIEGS |  |  |  |  |  | SAN DIEGO SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SODVILS |  |  |  |  |  | SODVILLE SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | STRU235 |  |  |  |  |  | STRUCTURE 235 |  |  |  |  |  |  |  | 0 |  |  |  | 42 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TAFT_S |  |  |  |  |  | TAFT SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TILDENS |  |  |  |  |  | TILDEN SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TINTOPS |  |  |  |  |  | TINTOP SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TURTLECK |  |  |  |  |  | TURTLE CREEK |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TWNPINS |  |  |  |  |  | TWIN PINES SUB |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TWNPNSW |  |  |  |  |  | TWIN PINES GOAB SWIT |  |  |  |  |  |  |  | 0 |  |  |  | 41 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TXBRINS |  |  |  |  |  | TEXAS BRINE SUB |  |  |  |  |  |  |  | 1 |  |  |  | 49 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | UVALDSW |  |  |  |  |  | UVALDE SWITCH |  |  |  |  |  |  |  | 0 |  |  |  | 11 |  |  |  |  |  |  |  |  |  | 4 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | UVLDES |  |  |  |  |  | UVALDE SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | VNDBLTS |  |  |  |  |  | VANDERBILT DIST SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | VNHUMBS |  |  |  |  |  | VAN HUMBLE SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | VNVLKS |  |  |  |  |  | VAN VLECK SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | VNVLKSW |  |  |  |  |  | VAN VLECK SWITCH |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | W_UVALS |  |  |  |  |  | WEST UVALDE SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WCRYSTS |  |  |  |  |  | WEST CRYSTAL CITY SU |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WGWSTS |  |  |  |  |  | WEST GEORGE WEST SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NumUBus | Islandnum | Fcomp |  |  |  |  |  |  | Fstatus |  |  |  |  |  |  |  | Fkv |  |  | Fstn |  |  |  |  |  | stnname |  |  |  |  |  |  |  | FBLI |  |  |  | RTUpref |  |  |  |  |  |  |  |  |  | N |  |
|  |  | STEC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WSINTOS |  |  |  |  |  | WEST SINTON SUB |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WSINTSW |  |  |  |  |  | WEST SINTON SWITCH |  |  |  |  |  |  |  | 0 |  |  |  | 26 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 138 |  |  | OAKS9 |  |  |  |  |  | OAKS SUB |  |  |  |  |  |  |  | 0 |  |  |  | 16 |  |  |  |  |  |  |  |  |  | 2 |  |
| 21 | 51 | AEP |  |  |  |  |  |  | b |  |  |  |  |  |  |  | 69 |  |  | ABEA |  |  |  |  |  | ABILENE EAST |  |  |  |  |  |  |  | 0 |  |  |  | 6 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ABPG |  |  |  |  |  | ABILENE PLANT |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ABRC |  |  |  |  |  | ABILENE RAINY CREEK |  |  |  |  |  |  |  | 0 |  |  |  | 7 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ABVT |  |  |  |  |  | ABILENE VOGEL TAP |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ALBANY |  |  |  |  |  | ALBANY CSW |  |  |  |  |  |  |  | 1 |  |  |  | 2 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BAIR |  |  |  |  |  | BAIRD |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HUB2 |  |  |  |  |  | HUBBARD BSTR 2 |  |  |  |  |  |  |  | 1 |  |  |  | 9 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PUTN |  |  |  |  |  | PUTNAM 138kv |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | THRM |  |  |  |  |  | THROCKMORTON |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 12 |  |  | ABPG |  |  |  |  |  | ABILENE PLANT |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 69 |  |  | ABED |  |  |  |  |  | ABILENE ELMDALE DEMA |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ABRP |  |  |  |  |  | ABILENE ROBERTSON PR |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ABWA |  |  |  |  |  | ABILENE WALNUT |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ALBNY_FD |  |  |  |  |  | ALBANY FOUNDRY |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BUKB |  |  |  |  |  | BUSH KNOB CSW |  |  |  |  |  |  |  | 1 |  |  |  | 8 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CLFK |  |  |  |  |  | CLEARFORK TAP |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CLYD |  |  |  |  |  | CLYDE |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CLYM |  |  |  |  |  | CLYDE MAGNOLIA |  |  |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  |  |  | 5 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FTFP |  |  |  |  |  | FORT PHANTOM PLANT P |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HUB1 |  |  |  |  |  | HUBBARD BSTR 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HUB1_TAP |  |  |  |  |  | HUBBARD BSTR 1 TAP |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MRAN |  |  |  |  |  | MORAN CSW |  |  |  |  |  |  |  | 1 |  |  |  | 3 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NUGE |  |  |  |  |  | NUGENT |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ONYS |  |  |  |  |  | ONYX SWITCHING STATI |  |  |  |  |  |  |  | 1 |  |  |  | 5 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PHAN |  |  |  |  |  | FORT PHANTOM |  |  |  |  |  |  |  | 0 |  |  |  | 4 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WTU_DETP |  |  |  |  |  | DENTON TAP |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WTU_DNTV |  |  |  |  |  | WTU DENTON |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | BEPC |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 69 |  |  | ALBANY1 |  |  |  |  |  | ALBANY TMPP |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BUSHKNOB |  |  |  |  |  | BUSH KNOB TMPP |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MORAN |  |  |  |  |  | MORAN TMPP |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 17 | 110 | TNMP |  |  |  |  |  |  | b |  |  |  |  |  |  |  | 69 |  |  | WICKETT |  |  |  |  |  | WICKETT TNP |  |  |  |  |  |  |  | 1 |  |  |  | 4 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WINK |  |  |  |  |  | WINK TNP |  |  |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  |  |  | 5 |  |
|  |  |  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 69 |  |  | AAPIPELN |  |  |  |  |  | AA PIPELINE TNP |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CALIF_TN |  |  |  |  |  | CALIFORNIA TNP |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | COCHISE |  |  |  |  |  | COCHISE TNP |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FLAT_TOP |  |  |  |  |  | FLAT TOP |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | IH20 |  |  |  |  |  | IH 20 |  |  |  |  |  |  |  | 1 |  |  |  | 2 |  |  |  |  |  |  |  |  |  | 5 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | KERMIT_1 |  |  |  |  |  | KERMIT 1 TNP |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | KERMIT_2 |  |  |  |  |  | KERMIT 2 TNP |  |  |  |  |  |  |  | 2 |  |  |  | 5 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | KEYSTONE |  |  |  |  |  | KEYSTONE TNP |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LNSTRTAP |  |  |  |  |  | LONESTAR TAP |  |  |  |  |  |  |  | 0 |  |  |  | 6 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LONESTAR |  |  |  |  |  | LONESTAR |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PECOS |  |  |  |  |  | PECOS |  |  |  |  |  |  |  | 3 |  |  |  | 3 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PYOTE |  |  |  |  |  | PYOTE |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NumUBus | Islandnum | Fcomp |  |  |  |  |  |  | Fstatus |  |  |  |  |  |  |  | Fkv |  |  | Fstn |  |  |  |  |  | stnname |  |  |  |  |  |  |  | FBLI |  |  |  | RTUpref |  |  |  |  |  |  |  |  |  | N |  |
|  |  | TNMP |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | REEVSCO4 |  |  |  |  |  | REEVES COUNTY4 TNP |  |  |  |  |  |  |  | 1 |  |  |  | 7 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | STAFBLVD |  |  |  |  |  | STAFFORD BLVD |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TOYAH |  |  |  |  |  | TOYAH |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WNKLRCO6 |  |  |  |  |  | WINKLER COUNTY 6 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WORSHAM |  |  |  |  |  | WORSHAM |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 | 64 | AEP |  |  |  |  |  |  | b |  |  |  |  |  |  |  | 69 |  |  | AIRP |  |  |  |  |  | AIR PRODUCTS CSW |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SHEF |  |  |  |  |  | SHEFFIELD |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 138 |  |  | INDN |  |  |  |  |  | INDIAN MESA |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MCAN_SW |  |  |  |  |  | MCCAMEY NORTH SW |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MESAV_SW |  |  |  |  |  | MESA VIEW SW |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 34 |  |  | INDNENR |  |  |  |  |  | DESERT SKY |  |  |  |  |  |  |  | 0 |  |  |  | 2 |  |  |  |  |  |  |  |  |  | 5 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | INDNNWP |  |  |  |  |  | INDIAN MESA NWP |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 69 |  |  | ARPT |  |  |  |  |  | AIR PRODUCTS TAP CSW |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | IRAN |  |  |  |  |  | IRAAN |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MART |  |  |  |  |  | MARATHON YATES TAP |  |  |  |  |  |  |  | 1 |  |  |  | 3 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MDSC |  |  |  |  |  | DISCOVERY CANYON |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | YATW_SW |  |  |  |  |  | WEST YATES SW |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 138 |  |  | INDNENR |  |  |  |  |  | DESERT SKY |  |  |  |  |  |  |  | 0 |  |  |  | 2 |  |  |  |  |  |  |  |  |  | 5 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | INDNNWP |  |  |  |  |  | INDIAN MESA NWP |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MCAM |  |  |  |  |  | MCCAMEY |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MESAVIEW |  |  |  |  |  | MESA VIEW |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | YATW_SW |  |  |  |  |  | WEST YATES SW |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | LCRA |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 138 |  |  | WESTYA |  |  |  |  |  | WEST YATES 1 |  |  |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  |  |  | 6 |  |
| 14 | 27 | ONCOR |  |  |  |  |  |  | b |  |  |  |  |  |  |  | 138 |  |  | ANATP |  |  |  |  |  | ANNA SWITCH TAP |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WHTMD |  |  |  |  |  | WHITE MOUND |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 138 |  |  | CLIMAXPO |  |  |  |  |  | CLIMAX POD |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PRCTN |  |  |  |  |  | PRINCETON |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | STNPT |  |  |  |  |  | STONEY POINT |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | VAEGC |  |  |  |  |  | VAN ALSTYNE EAST |  |  |  |  |  |  |  | 1 |  |  |  | 3 |  |  |  |  |  |  |  |  |  | 2 |  |
|  |  | RCEC |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 138 |  |  | EVANALRC |  |  |  |  |  | EAST VAN ALSTYNE |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | TNMP |  |  |  |  |  |  | b |  |  |  |  |  |  |  | 69 |  |  | WHITEWRT |  |  |  |  |  | WHITEWRIGHT |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 69 |  |  | BLUERDGE |  |  |  |  |  | BLUE RIDGE |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CLIMAX |  |  |  |  |  | CLIMAX TNP |  |  |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  |  |  | 8 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FRMRSVLE |  |  |  |  |  | FARMERSVILLE TNP |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FRNTRTAP |  |  |  |  |  | FRONTIER TAP TNP |  |  |  |  |  |  |  | 0 |  |  |  | 2 |  |  |  |  |  |  |  |  |  | 3 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FRONTIER |  |  |  |  |  | FRONTIER TNP |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LEONARD |  |  |  |  |  | LEONARD |  |  |  |  |  |  |  | 2 |  |  |  | 4 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LONGNECK |  |  |  |  |  | LONGNECK |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TRENTON |  |  |  |  |  | TRENTON TNP |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 138 |  |  | CLIMAX |  |  |  |  |  | CLIMAX TNP |  |  |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  |  |  | 8 |  |
| 12 | 49 | AEP |  |  |  |  |  |  | b |  |  |  |  |  |  |  | 69 |  |  | BENJ |  |  |  |  |  | BENJAMIN CSW |  |  |  |  |  |  |  | 1 |  |  |  | 6 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | EXTR |  |  |  |  |  | EXXON TRUSCOTT |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HSKL |  |  |  |  |  | HASKELL |  |  |  |  |  |  |  | 1 |  |  |  | 5 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | JOSS |  |  |  |  |  | JOSSELETT |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | KNXR |  |  |  |  |  | KNOX CITY REA |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MUND |  |  |  |  |  | MUNDAY CSW |  |  |  |  |  |  |  | 1 |  |  |  | 4 |  |  |  |  |  |  |  |  |  | 1 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ROCH |  |  |  |  |  | ROCHESTER CSW |  |  |  |  |  |  |  | 0 |  |  |  | 7 |  |  |  |  |  |  |  |  |  | 1 |  |
| NumUBus | Islandnum | Fcomp |  |  |  |  | Fstatus |  |  |  |  |  |  |  | Fkv |  |  |  | Fstn |  |  |  |  |  | stnname |  |  |  |  |  |  | FBLI |  |  |  |  | RTUpref |  |  |  |  |  |  |  |  | N |  |  |  |
|  |  | AEP |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WEIN |  |  |  |  |  | WEINERT |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 69 |  |  |  | GILL |  |  |  |  |  | GILLESPIE REA |  |  |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  |  |  |  |  | 4 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HASR |  |  |  |  |  | HASKELL REA |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HASTXTP |  |  |  |  |  | HASKEL TEXAS TAP |  |  |  |  |  |  | 0 |  |  |  |  | 3 |  |  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | KNXC |  |  |  |  |  | KNOX CITY |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TRUS |  |  |  |  |  | TRUSCOTT CSW |  |  |  |  |  |  | 1 |  |  |  |  | 2 |  |  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TXHS |  |  |  |  |  | HASKEL TEXAS |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | BEPC |  |  |  |  | U |  |  |  |  |  |  |  | 69 |  |  |  | BENJAMIN |  |  |  |  |  | BENJAMIN TMPP |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | GILESPIE |  |  |  |  |  | GILLESPIE TMPP |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | GOREE |  |  |  |  |  | GOREE |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MUNDAYR2 |  |  |  |  |  | MUNDAY TMPP |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ROCHSTER |  |  |  |  |  | ROCHESTER TMPP |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TRUSCOTT |  |  |  |  |  | TRUSCOTT TMPP |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 | 72 | AEP |  |  |  |  | b |  |  |  |  |  |  |  | 69 |  |  |  | HUMT |  |  |  |  |  | HUMBLE TAP |  |  |  |  |  |  | 0 |  |  |  |  | 2 |  |  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MCAM |  |  |  |  |  | MCCAMEY |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MIDW |  |  |  |  |  | MIDWAY LANE |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PHBL |  |  |  |  |  | BIG LAKE PHILLIP |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SCRS |  |  |  |  |  | SOUTH CROSS |  |  |  |  |  |  | 2 |  |  |  |  | 4 |  |  |  |  |  |  |  |  | 1 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SHME |  |  |  |  |  | SHELL MESA |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 69 |  |  |  | ATLB |  |  |  |  |  | ATLANTIC BEST |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ATLT |  |  |  |  |  | ATLANTIC BEST TAP |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BOBCATH |  |  |  |  |  | BOB CAT HILL |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | EXKE |  |  |  |  |  | EXXON KEMPER |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | POWF |  |  |  |  |  | POWELL FIELD |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | POWT |  |  |  |  |  | POWELL FIELD TAP |  |  |  |  |  |  | 0 |  |  |  |  | 3 |  |  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | RANK |  |  |  |  |  | RANKIN |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SHPO |  |  |  |  |  | SHELL POWELL |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | STRS |  |  |  |  |  | STRAUSS REA |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TEXN |  |  |  |  |  | TEXON |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TEXT |  |  |  |  |  | TEXON TAP |  |  |  |  |  |  | 0 |  |  |  |  | 1 |  |  |  |  |  |  |  |  | 4 |  |  |  |
| 10 | 61 | AEP |  |  |  |  | b |  |  |  |  |  |  |  | 69 |  |  |  | CEDH |  |  |  |  |  | CEDAR HILL CSW |  |  |  |  |  |  | 0 |  |  |  |  | 1 |  |  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | EDIT |  |  |  |  |  | EDITH |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MILE |  |  |  |  |  | MILES |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PANA |  |  |  |  |  | PAN AMERICAN |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 69 |  |  |  | AMBR |  |  |  |  |  | BRONTE AMBASSADOR |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ATBR |  |  |  |  |  | BRONTE ATLANTIC |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BRNT |  |  |  |  |  | BRONTE |  |  |  |  |  |  | 1 |  |  |  |  | 3 |  |  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | EXPE |  |  |  |  |  | PERKINS PROTHRO |  |  |  |  |  |  | 1 |  |  |  |  | 4 |  |  |  |  |  |  |  |  | 1 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ROBL |  |  |  |  |  | ROBERT LEE |  |  |  |  |  |  | 1 |  |  |  |  | 5 |  |  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SILR |  |  |  |  |  | SILVER REA |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SILT |  |  |  |  |  | SILVER TAP |  |  |  |  |  |  | 0 |  |  |  |  | 2 |  |  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SILV |  |  |  |  |  | SILVER |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SPEN |  |  |  |  |  | SPENCE PUMP |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SPRH |  |  |  |  |  | SPADE RANCH |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 83 | AEP |  |  |  |  | b |  |  |  |  |  |  |  | 69 |  |  |  | ALTAIR |  |  |  |  |  | ALTAIR |  |  |  |  |  |  | 0 |  |  |  |  | 2 |  |  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PARKER |  |  |  |  |  | PARKER |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 69 |  |  |  | B_GRAVEL |  |  |  |  |  | BB GRAVEL |  |  |  |  |  |  | 1 |  |  |  |  | 4 |  |  |  |  |  |  |  |  | 1 |  |  |  |
| NumUBus | Islandnum | Fcomp |  |  |  |  | Fstatus |  |  |  |  |  |  |  | Fkv |  |  |  | Fstn |  |  |  |  |  | stnname |  |  |  |  |  |  | FBLI |  |  |  |  | RTUpref |  |  |  |  |  |  |  |  | N |  |  |  |
|  |  | AEP |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | GARWDPMP |  |  |  |  |  | GARWOOD PUMP |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | GARWDRLF |  |  |  |  |  | GARWOOD RELIEF |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | GARWDTAP |  |  |  |  |  | GARWOOD TAP |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | IDEAL_ |  |  |  |  |  | IDEAL CEMENT |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | IDEAL_TP |  |  |  |  |  | IDEAL CEMENT TAP |  |  |  |  |  |  | 0 |  |  |  |  | 1 |  |  |  |  |  |  |  |  | 4 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PRAIRPMP |  |  |  |  |  | PRAIRIE PUMP |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | RIVER_SD |  |  |  |  |  | RIVERSIDE PUMP |  |  |  |  |  |  | 1 |  |  |  |  | 5 |  |  |  |  |  |  |  |  | 1 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TXI_TP |  |  |  |  |  | TEXAS INDUSTRIES TAP |  |  |  |  |  |  | 0 |  |  |  |  | 3 |  |  |  |  |  |  |  |  | 2 |  |  |  |
|  |  | STEC |  |  |  |  | U |  |  |  |  |  |  |  | 69 |  |  |  | PIONEERS |  |  |  |  |  | PIONEER |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9 | 6 | ONCOR |  |  |  |  | b |  |  |  |  |  |  |  | 138 |  |  |  | ARCTP |  |  |  |  |  | AIRCO TAP |  |  |  |  |  |  | 0 |  |  |  |  | 4 |  |  |  |  |  |  |  |  | 1 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BLKLD |  |  |  |  |  | BLACKLAND |  |  |  |  |  |  | 0 |  |  |  |  | 3 |  |  |  |  |  |  |  |  | 1 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | RHILL |  |  |  |  |  | ROSE HILL TU |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TRNTP |  |  |  |  |  | TERRELL NORTH TAP |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 138 |  |  |  | BLKLD |  |  |  |  |  | BLACKLAND |  |  |  |  |  |  | 1 |  |  |  |  | 3 |  |  |  |  |  |  |  |  | 1 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NWTTP |  |  |  |  |  | TERRELL NW |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | RCEC |  |  |  |  | U |  |  |  |  |  |  |  | 138 |  |  |  | BLDSW_RC |  |  |  |  |  | BLACKLAND SWITCH |  |  |  |  |  |  | 0 |  |  |  |  | 1 |  |  |  |  |  |  |  |  | 4 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | COMBINRC |  |  |  |  |  | ROSE HILL CSW |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | QUINL_RC |  |  |  |  |  | QUINLAND |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ROSHILRC |  |  |  |  |  | ROSE HILL |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TALTY_RC |  |  |  |  |  | TALTY |  |  |  |  |  |  | 1 |  |  |  |  | 2 |  |  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WIELD_RC |  |  |  |  |  | WIELAND |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WMUNS_RC |  |  |  |  |  | WEST MUNSON |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 54 | COGRLND |  |  |  |  | b |  |  |  |  |  |  |  | 138 |  |  |  | GN_S_I |  |  |  |  |  | GREENVILLE STEAM |  |  |  |  |  |  | 0 |  |  |  |  | 3 |  |  |  |  |  |  |  |  | 1 |  |  |  |
|  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 69 |  |  |  | GN_S_I |  |  |  |  |  | GREENVILLE STEAM |  |  |  |  |  |  | 0 |  |  |  |  | 3 |  |  |  |  |  |  |  |  | 1 |  |  |  |
|  |  | GEUS |  |  |  |  | b |  |  |  |  |  |  |  | 69 |  |  |  | STEAM |  |  |  |  |  | STEAM |  |  |  |  |  |  | 0 |  |  |  |  | 2 |  |  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 14 |  |  |  | DIESEL |  |  |  |  |  | DIESEL |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 69 |  |  |  | DENT_RD |  |  |  |  |  | DENTON ROAD |  |  |  |  |  |  | 1 |  |  |  |  | 4 |  |  |  |  |  |  |  |  | 1 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DIESEL |  |  |  |  |  | DIESEL |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | IND_PK_D |  |  |  |  |  | INDUSTRIAL PARK GR |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LTV_D |  |  |  |  |  | LTV TMPP |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MAMIE_D |  |  |  |  |  | MAMIE |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ONEAL |  |  |  |  |  | ONEAL |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TERREL_D |  |  |  |  |  | TERREL |  |  |  |  |  |  | 2 |  |  |  |  | 1 |  |  |  |  |  |  |  |  | 4 |  |  |  |
|  | 70 | AEP |  |  |  |  | b |  |  |  |  |  |  |  | 69 |  |  |  | CRAN |  |  |  |  |  | CRANE CSW |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CRANTAP2 |  |  |  |  |  | CRANE TAP 2 |  |  |  |  |  |  | 0 |  |  |  |  | 3 |  |  |  |  |  |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  | U |  |  |  |  |  |  |  | 69 |  |  |  | CRAN_AIR |  |  |  |  |  | CRANE COUNTY AIR |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DUN2 |  |  |  |  |  | DUNE FIELD |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DUNETAP |  |  |  |  |  | DUNE FIELD TAP |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | GUCA |  |  |  |  |  | CRANE GULF 1 |  |  |  |  |  |  | 2 |  |  |  |  | 1 |  |  |  |  |  |  |  |  | 4 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | GUCB |  |  |  |  |  | CRANE GULF 2 |  |  |  |  |  |  | 1 |  |  |  |  | 2 |  |  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | GUCT |  |  |  |  |  | CRANE GULF TAP |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MCEL |  |  |  |  |  | MCELROY |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TES_CRAN |  |  |  |  |  | TES CRANE TAP |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TNMP |  |  |  |  |  | TEXAS NEW MEXICO PIP |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 127 | LCRA |  |  |  |  | b |  |  |  |  |  |  |  | 69 |  |  |  | MOUNTO |  |  |  |  |  | MOUNTAIN TOP |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 138 |  |  |  | DEVIHI |  |  |  |  |  | DEVILS HILL |  |  |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  |  |  |  |  | 3 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HIGH32 |  |  |  |  |  | HIGHWAY 32 |  |  |  |  |  |  | 1 |  |  |  |  | 2 |  |  |  |  |  |  |  |  | 3 |  |  |  |
| NumUBus | Islandnum | Fcomp |  |  |  | Fstatus |  |  |  |  |  | Fkv |  |  |  |  |  | Fstn |  |  |  |  |  | stnname |  |  |  |  |  | FBLI |  |  |  |  |  | RTUpref |  |  |  |  |  |  | N |  |  |  |  |  |  |
|  |  | LCRA |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HUNTER |  |  |  |  |  | HUNTER LCRA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | U |  |  |  |  |  | 4 |  |  |  |  |  | CANYHY |  |  |  |  |  | CANYON DAM HYDRO |  |  |  |  |  | 0 |  |  |  |  |  | 3 |  |  |  |  |  |  | 3 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 69 |  |  |  |  |  | BLANCO |  |  |  |  |  | BLANCO |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DEVIHI |  |  |  |  |  | DEVILS HILL |  |  |  |  |  | 0 |  |  |  |  |  | 1 |  |  |  |  |  |  | 3 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HIGH32 |  |  |  |  |  | HIGHWAY 32 |  |  |  |  |  | 0 |  |  |  |  |  | 2 |  |  |  |  |  |  | 3 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WIMBER |  |  |  |  |  | WIMBERLEY |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 138 |  |  |  |  |  | CANYHY |  |  |  |  |  | CANYON DAM HYDRO |  |  |  |  |  | 0 |  |  |  |  |  | 3 |  |  |  |  |  |  | 3 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CRANMI |  |  |  |  |  | CRANES MILL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FISCHE |  |  |  |  |  | FISCHER |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SATTLE |  |  |  |  |  | SATTLER |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 | 4 | ONCOR |  |  |  | b |  |  |  |  |  | 138 |  |  |  |  |  | NPKTP |  |  |  |  |  | NIPAK TAP |  |  |  |  |  | 0 |  |  |  |  |  | 3 |  |  |  |  |  |  | 1 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | OKGTP |  |  |  |  |  | OAK GROVE TAP |  |  |  |  |  | 0 |  |  |  |  |  | 4 |  |  |  |  |  |  | 1 |  |  |  |  |  |  |
|  |  |  |  |  |  | U |  |  |  |  |  | 138 |  |  |  |  |  | CCPMP |  |  |  |  |  | CEDAR CREEK PUMP |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CDCRK |  |  |  |  |  | CEDAR CREEK |  |  |  |  |  | 2 |  |  |  |  |  | 1 |  |  |  |  |  |  | 3 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | KMPSO |  |  |  |  |  | KEMP SOUTH |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NIPAK |  |  |  |  |  | NIPAK |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SVPTS |  |  |  |  |  | SEVEN POINTS |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | RCEC |  |  |  | b |  |  |  |  |  | 138 |  |  |  |  |  | OAKGRVRC |  |  |  |  |  | OAK GROVE |  |  |  |  |  | 0 |  |  |  |  |  | 2 |  |  |  |  |  |  | 2 |  |  |  |  |  |  |
|  |  |  |  |  |  | U |  |  |  |  |  | 138 |  |  |  |  |  | RAND_RC |  |  |  |  |  | RANDADO |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SCURY_RC |  |  |  |  |  | SCURRY POD |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 103 | TNMP |  |  |  | b |  |  |  |  |  | 138 |  |  |  |  |  | AMOCOOIL |  |  |  |  |  | AMOCO OIL COGEN |  |  |  |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  |  | 7 |  |  |  |  |  |  |
|  |  |  |  |  |  | U |  |  |  |  |  | 14 |  |  |  |  |  | AMOCOOIL |  |  |  |  |  | AMOCO OIL COGEN |  |  |  |  |  | 0 |  |  |  |  |  | 1 |  |  |  |  |  |  | 7 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 18 |  |  |  |  |  | AMOCOOIL |  |  |  |  |  | AMOCO OIL COGEN |  |  |  |  |  | 0 |  |  |  |  |  | 1 |  |  |  |  |  |  | 7 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 138 |  |  |  |  |  | AMOCOOIL |  |  |  |  |  | AMOCO OIL COGEN |  |  |  |  |  | 0 |  |  |  |  |  | 1 |  |  |  |  |  |  | 7 |  |  |  |  |  |  |
| 6 | 2 | ONCOR |  |  |  | b |  |  |  |  |  | 138 |  |  |  |  |  | ALLEN |  |  |  |  |  | ALLEN 1 |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ALNTH |  |  |  |  |  | ALLEN NORTH |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CMBVL |  |  |  |  |  | CHAMBERSVILLE POD |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MKNTI |  |  |  |  |  | MCKINNEY TEXAS INSTR |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | U |  |  |  |  |  | 138 |  |  |  |  |  | ALNTH |  |  |  |  |  | ALLEN NORTH |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MKNNY |  |  |  |  |  | MCKINNEY |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MKNSW |  |  |  |  |  | MCKINNEY SOUTHWEST |  |  |  |  |  | 2 |  |  |  |  |  | 1 |  |  |  |  |  |  | 6 |  |  |  |  |  |  |
|  |  | RCEC |  |  |  | U |  |  |  |  |  | 138 |  |  |  |  |  | MCKSW_RC |  |  |  |  |  | MCKINNEY SW POD DIST |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 13 | ONCOR |  |  |  | b |  |  |  |  |  | 138 |  |  |  |  |  | DIBOL |  |  |  |  |  | DIBOLL |  |  |  |  |  | 2 |  |  |  |  |  | 1 |  |  |  |  |  |  | 3 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HUDSN |  |  |  |  |  | HUDSON |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LFPTP |  |  |  |  |  | LUFKIN PERSHING TAP |  |  |  |  |  | 0 |  |  |  |  |  | 3 |  |  |  |  |  |  | 1 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LFSTE |  |  |  |  |  | LUFKIN SWITCH TAP EA |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TXFND |  |  |  |  |  | TEXAS FOUNDRIES |  |  |  |  |  | 0 |  |  |  |  |  | 4 |  |  |  |  |  |  | 1 |  |  |  |  |  |  |
|  |  |  |  |  |  | U |  |  |  |  |  | 138 |  |  |  |  |  | DIBSP |  |  |  |  |  | DIBOLL SOUTHERN PINE |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DIBSW |  |  |  |  |  | DIBOLL SWITCH |  |  |  |  |  | 0 |  |  |  |  |  | 2 |  |  |  |  |  |  | 1 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HAMLIN |  |  |  |  |  | HAMLIN TEXAS CO |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LFSTW |  |  |  |  |  | LUFKIN SOUTH TAP WES |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LPRSH |  |  |  |  |  | LUFKIN PERSHING |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | TEXLA |  |  |  | U |  |  |  |  |  | 138 |  |  |  |  |  | DIBLWT4 |  |  |  |  |  | DIBOLL SE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 77 |  |  |  |  | U |  |  |  |  |  | 69 |  |  |  |  |  | HARRELL |  |  |  |  |  | HARRELL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | TNMP |  |  |  | b |  |  |  |  |  | 69 |  |  |  |  |  | TNFS |  |  |  |  |  | TEXAS NEW MEXICO |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WTU_WHTB |  |  |  |  |  | WHITE BAKER |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | U |  |  |  |  |  | 69 |  |  |  |  |  | ARMDL02 |  |  |  |  |  | ARMADILLO |  |  |  |  |  | 1 |  |  |  |  |  | 3 |  |  |  |  |  |  | 1 |  |  |  |  |  |  |
| NumUBus | Islandnum | Fcomp |  |  | Fstatus |  |  |  |  |  | Fkv |  |  |  |  | Fstn |  |  |  |  |  |  | stnname |  |  |  |  |  | FBLI |  |  |  |  |  | RTUpref |  |  |  |  |  | N |  |  |  |  |  |  |  |  |
|  |  | TNMP |  |  |  |  |  |  |  |  |  |  |  |  |  | PUCKETT |  |  |  |  |  |  | PUCKETT |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PUCKTAP |  |  |  |  |  |  | PUCKETT TAP |  |  |  |  |  | 0 |  |  |  |  |  | 1 |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SANDRSON |  |  |  |  |  |  | SANDERSON |  |  |  |  |  | 4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WTU_TNNG |  |  |  |  |  |  | NORTHERN NATURAL GAS |  |  |  |  |  | 2 |  |  |  |  |  | 2 |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |
|  | 79 | AEP |  |  | b |  |  |  |  |  | 69 |  |  |  |  | BRYR |  |  |  |  |  |  | BRYANTS RANCH |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | U |  |  |  |  |  | 14 |  |  |  |  | PRES |  |  |  |  |  |  | PRESIDIO |  |  |  |  |  | 0 |  |  |  |  |  | 2 |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 69 |  |  |  |  | ATKN |  |  |  |  |  |  | ATKINSON RANCH |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CIEN |  |  |  |  |  |  | CIENEGA RGEC |  |  |  |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | PRES |  |  |  |  |  |  | PRESIDIO |  |  |  |  |  | 1 |  |  |  |  |  | 2 |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SHAF |  |  |  |  |  |  | SHAFTER GOLDMINE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 109 | TNMP |  |  | b |  |  |  |  |  | 69 |  |  |  |  | CLIFTON1 |  |  |  |  |  |  | CLIFTON 1 TNP |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HAMLTNCO |  |  |  |  |  |  | HAMILTON COUNTY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | WALNTSPR |  |  |  |  |  |  | WALNUT SPRINGS TNP |  |  |  |  |  | 1 |  |  |  |  |  | 2 |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |
|  |  |  |  |  | U |  |  |  |  |  | 69 |  |  |  |  | CLFTNTAP |  |  |  |  |  |  | CLIFTON TAP TNP |  |  |  |  |  | 0 |  |  |  |  |  | 1 |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CLIFTON2 |  |  |  |  |  |  | CLIFTON 2 TNP |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HICOTAP |  |  |  |  |  |  | HICO TAP |  |  |  |  |  | 0 |  |  |  |  |  | 3 |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | HICOTN |  |  |  |  |  |  | HICO |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MERDNTAP |  |  |  |  |  |  | MERIDIAN TAP |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MERID_TN |  |  |  |  |  |  | MERIDIAN TNP |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 | 15 | BEPC |  |  | U |  |  |  |  |  | 138 |  |  |  |  | FFD |  |  |  |  |  |  | FAIRFIELD TMPP |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | ONCOR |  |  | b |  |  |  |  |  | 138 |  |  |  |  | BBNTP |  |  |  |  |  |  | BIG BROWN TAP |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BLKTP |  |  |  |  |  |  | BLACKFOOT TAP |  |  |  |  |  | 0 |  |  |  |  |  | 3 |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FRFWS |  |  |  |  |  |  | FAIRFIELD WEST |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | U |  |  |  |  |  | 138 |  |  |  |  | BBMN1 |  |  |  |  |  |  | BIG BROWN MINE 1 |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BBMN2 |  |  |  |  |  |  | BIG BROWN MINE 2 |  |  |  |  |  | 2 |  |  |  |  |  | 1 |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BLKFT |  |  |  |  |  |  | BLACKFOOT |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FRFBE |  |  |  |  |  |  | FAIRFIELD TU |  |  |  |  |  | 0 |  |  |  |  |  | 2 |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |
|  | 33 | ONCOR |  |  | b |  |  |  |  |  | 138 |  |  |  |  | IRBTP |  |  |  |  |  |  | IRON BRIDGE TAP |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LBRPD |  |  |  |  |  |  | LIBERTY POD TU |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | U |  |  |  |  |  | 138 |  |  |  |  | EMORY |  |  |  |  |  |  | EMORY TU |  |  |  |  |  | 2 |  |  |  |  |  | 1 |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | EMPOD |  |  |  |  |  |  | EMORY POD |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ENTPI |  |  |  |  |  |  | ENTERPRISE POI |  |  |  |  |  | 1 |  |  |  |  |  | 2 |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | IRBRG |  |  |  |  |  |  | IRON BRIDGE |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | TNMP |  |  | U |  |  |  |  |  | 138 |  |  |  |  | EMORYTN |  |  |  |  |  |  | EMORY TNP |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 71 |  |  |  | U |  |  |  |  |  | 69 |  |  |  |  | DUTTON |  |  |  |  |  |  | DUTTON |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | AEP |  |  | b |  |  |  |  |  | 69 |  |  |  |  | BRDY |  |  |  |  |  |  | BRADY NORTH |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CSSB |  |  |  |  |  |  | CAMP SAN SABA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MCLC |  |  |  |  |  |  | MCEC TAP |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | U |  |  |  |  |  | 69 |  |  |  |  | BRDC |  |  |  |  |  |  | BRADY SOUTH EAST TAP |  |  |  |  |  | 2 |  |  |  |  |  | 2 |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BRDS |  |  |  |  |  |  | SOUTH BRADY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MCEC |  |  |  |  |  |  | MCCOULLOUGH EDEN COO |  |  |  |  |  | 0 |  |  |  |  |  | 1 |  |  |  |  |  | 4 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MELV |  |  |  |  |  |  | MELVIN |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 73 | AEP |  |  | b |  |  |  |  |  | 69 |  |  |  |  | MRFA |  |  |  |  |  |  | MARFA AIRPORT |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | U |  |  |  |  |  | 69 |  |  |  |  | ESPY |  |  |  |  |  |  | ESPY WELLS |  |  |  |  |  | 1 |  |  |  |  |  | 2 |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FORTDA |  |  |  |  |  |  | FORT DAVIS GEN |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | FTDA |  |  |  |  |  |  | FORT DAVIS |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | POND |  |  |  |  |  |  | PONDER KENEDY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NumUBus | Islandnum | Fcomp |  | Fstatus |  |  |  |  |  | Fkv |  |  |  | Fstn |  |  |  |  |  |  |  | stnname |  |  |  |  |  | FBLI |  |  |  |  | RTUpref |  |  |  |  |  |  | N |  |  |  |  |  |  |  |  |  |
|  |  | AEP |  |  |  |  |  |  |  |  |  |  |  | VALT |  |  |  |  |  |  |  | VALENTINE TAP |  |  |  |  |  | 2 |  |  |  |  | 1 |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |
|  | 81 |  |  | U |  |  |  |  |  | 69 |  |  |  | NEWJUNC |  |  |  |  |  |  |  | NEW JUNCTION |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | AEN |  | U |  |  |  |  |  | 69 |  |  |  | SEGOVTP |  |  |  |  |  |  |  | SEGOVIA TAP |  |  |  |  |  | 0 |  |  |  |  | 1 |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |
|  |  | AEP |  | b |  |  |  |  |  | 69 |  |  |  | KMJC |  |  |  |  |  |  |  | KIMBLE JUNCTION |  |  |  |  |  | 1 |  |  |  |  | 2 |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | MASW |  |  |  |  |  |  |  | MASON SWITCHING STAT |  |  |  |  |  | 0 |  |  |  |  | 3 |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |
|  |  |  |  | U |  |  |  |  |  | 69 |  |  |  | SHLO |  |  |  |  |  |  |  | SHELL LONDON |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | STRT |  |  |  |  |  |  |  | STREETER |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | LCRA |  | U |  |  |  |  |  | 69 |  |  |  | SEGOVI |  |  |  |  |  |  |  | SEGOVIA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 125 | PUB |  | b |  |  |  |  |  | 69 |  |  |  | MIDTOWN |  |  |  |  |  |  |  | MIDTOWN |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | PRICE_RD |  |  |  |  |  |  |  | PRICE ROAD |  |  |  |  |  | 1 |  |  |  |  | 2 |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | SIXTH_ST |  |  |  |  |  |  |  | 6TH STREET |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | UNION_CA |  |  |  |  |  |  |  | UNION CARBIDE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | U |  |  |  |  |  | 69 |  |  |  | 802_SUB |  |  |  |  |  |  |  | FM 802 |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | AIRPORT |  |  |  |  |  |  |  | AIRPORT PUB |  |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  |  |  | 4 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | FILTER_P |  |  |  |  |  |  |  | FILTER PLANT |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | FORT_BRO |  |  |  |  |  |  |  | FORT BROWN |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | WATERPOR |  |  |  |  |  |  |  | WATERPORT |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 | 36 | ONCOR |  | b |  |  |  |  |  | 69 |  |  |  | RYLTY |  |  |  |  |  |  |  | ROYALTY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | U |  |  |  |  |  | 69 |  |  |  | COYAN |  |  |  |  |  |  |  | COYANOSA |  |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | NNTRL |  |  |  |  |  |  |  | NORTHERN NATURAL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | WFCMP |  |  |  |  |  |  |  | WOLFCAMP |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | WLFTP |  |  |  |  |  |  |  | WOLFCAMP TAP |  |  |  |  |  | 0 |  |  |  |  | 2 |  |  |  |  |  |  | 4 |  |  |  |  |  |  |  |  |  |
|  | 39 | ONCOR |  | b |  |  |  |  |  | 138 |  |  |  | CRM8T |  |  |  |  |  |  |  | CRMWD 8 TAP |  |  |  |  |  | 0 |  |  |  |  | 2 |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | LIQAR |  |  |  |  |  |  |  | LIQUID AIR |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | U |  |  |  |  |  | 138 |  |  |  | CRMW8 |  |  |  |  |  |  |  | CRMWD NO 8 |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | GLNHV |  |  |  |  |  |  |  | GLENHAVEN |  |  |  |  |  | 3 |  |  |  |  | 1 |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | ODESA |  |  |  |  |  |  |  | ODESSA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | TDWGL |  |  |  |  |  |  |  | TIDEWATER GLENHAVEN |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 43 | ONCOR |  | b |  |  |  |  |  | 69 |  |  |  | NLNWT |  |  |  |  |  |  |  | NOLAN WEST TAP |  |  |  |  |  | 0 |  |  |  |  | 2 |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |
|  |  |  |  | U |  |  |  |  |  | 69 |  |  |  | LNSTC |  |  |  |  |  |  |  | LONE STAR CEMENT |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | MRYNL |  |  |  |  |  |  |  | MARYNEAL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | MRYTP |  |  |  |  |  |  |  | MARYNEAL TAP |  |  |  |  |  | 0 |  |  |  |  | 1 |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | NOLNW |  |  |  |  |  |  |  | NOLAN WEST |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 57 | DENTON |  | b |  |  |  |  |  | 69 |  |  |  | LOCUST_D |  |  |  |  |  |  |  | LOCUST |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | SPNCER |  |  |  |  |  |  |  | SPENCER TMPP |  |  |  |  |  | 0 |  |  |  |  | 2 |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |
|  |  |  |  | U |  |  |  |  |  | 69 |  |  |  | HICKRY_D |  |  |  |  |  |  |  | HICKORY |  |  |  |  |  | 2 |  |  |  |  | 3 |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | KING_D |  |  |  |  |  |  |  | KING |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | N_LAKE_D |  |  |  |  |  |  |  | NORTH LAKE D |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | WOODROW |  |  |  |  |  |  |  | WOODROW |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | TMPA |  | b |  |  |  |  |  | 69 |  |  |  | N_DENT |  |  |  |  |  |  |  | NORTH DENTON |  |  |  |  |  | 0 |  |  |  |  | 1 |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |
|  | 67 | AEP |  | b |  |  |  |  |  | 69 |  |  |  | HATC |  |  |  |  |  |  |  | HATCHEL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | ROBT |  |  |  |  |  |  |  | ROBERTS |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | U |  |  |  |  |  | 69 |  |  |  | CLIM |  |  |  |  |  |  |  | CLIMAX BRADSHAW |  |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  |  |  | 4 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | HAPV |  |  |  |  |  |  |  | HAPPY VALLEY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | TUSC |  |  |  |  |  |  |  | TUSCOLA |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | WINT |  |  |  |  |  |  |  | WINTERS |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 74 | AEP |  | b |  |  |  |  |  | 69 |  |  |  | ELDO |  |  |  |  |  |  |  | ELDORADO |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NumUBus | Islandnum | Fcomp | Fstatus |  |  |  |  | Fkv |  |  |  |  | Fstn |  |  |  |  |  |  |  | stnname |  |  |  |  |  | FBLI |  |  |  | RTUpref |  |  |  |  |  |  |  | N |  |  |  |  |  |  |  |  |  |  |
|  |  | AEP |  |  |  |  |  |  |  |  |  |  | SHBT |  |  |  |  |  |  |  | SHELL BAILEY TAP |  |  |  |  |  | 0 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | FMCK |  |  |  |  |  |  |  | FORT MCKAVETT |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MIDV |  |  |  |  |  |  |  | MIDDLE VALLEY |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | PAGE |  |  |  |  |  |  |  | PAGE FIELD |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SHBA |  |  |  |  |  |  |  | SHELL BAILY SONR |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 | 1 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | GVGLF |  |  |  |  |  |  |  | GRANDVIEW GULF |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | FLSSN |  |  |  |  |  |  |  | FILES SINCLAIR |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MYPRL |  |  |  |  |  |  |  | MAYPEARL TU |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MYPTX |  |  |  |  |  |  |  | MAYPEARL TEXACO |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |
|  | 8 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | MXTAP |  |  |  |  |  |  |  | MEXIA TAP |  |  |  |  |  | 1 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SMBMG |  |  |  |  |  |  |  | SIMSBORO MAGNOLIA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | WORJC |  |  |  |  |  |  |  | WORTHAM JUNCTION |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | WORGP |  |  |  |  |  |  |  | WORTHAM GULF PUMP |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | WRGPT |  |  |  |  |  |  |  | WORTHAM GULF TAP |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | WRTHM |  |  |  |  |  |  |  | WORTHAM |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 11 | BEPC | U |  |  |  |  | 138 |  |  |  |  | BGS |  |  |  |  |  |  |  | BEARGRASS TMPP |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | ONCOR | b |  |  |  |  | 138 |  |  |  |  | AMGTP |  |  |  |  |  |  |  | AMERIGAS TAP |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | BRGRS |  |  |  |  |  |  |  | BEARGRASS TU |  |  |  |  |  | 2 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | AMGAS |  |  |  |  |  |  |  | AMERIGAS |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | NUCOR |  |  |  |  |  |  |  | NUCOR |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  | 20 | BEPC | U |  |  |  |  | 69 |  |  |  |  | DELEON |  |  |  |  |  |  |  | DELEON |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | ONCOR | b |  |  |  |  | 69 |  |  |  |  | CMHTP |  |  |  |  |  |  |  | COMYN HUMBLE TAP |  |  |  |  |  | 0 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | DLMTP |  |  |  |  |  |  |  | DE LEON MAGNOLIA TAP |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | CMHBL |  |  |  |  |  |  |  | COMYN HUMBLE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | DLEON |  |  |  |  |  |  |  | DE LEON |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  | 28 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | CUMBY |  |  |  |  |  |  |  | CUMBY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | RCEC | U |  |  |  |  | 69 |  |  |  |  | KIOWA_RC |  |  |  |  |  |  |  | KIOWA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SUNYP_RC |  |  |  |  |  |  |  | SUN VALLEY COOP POD |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | TNMP | U |  |  |  |  | 69 |  |  |  |  | LONE_OAK |  |  |  |  |  |  |  | LONE OAK |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |
|  | 29 | ONCOR | b |  |  |  |  | 138 |  |  |  |  | NWYTP |  |  |  |  |  |  |  | NW WYLIE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | WYLTP |  |  |  |  |  |  |  | WYLIE TAP |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | LAVON |  |  |  |  |  |  |  | LAVON |  |  |  |  |  | 4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | LVNPM |  |  |  |  |  |  |  | LAVON PUMP 2 |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | WYLPM |  |  |  |  |  |  |  | WYLIE PUMP |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |
|  | 37 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | BSCTP |  |  |  |  |  |  |  | BIG SPRING CRMWD TAP |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | CHATP |  |  |  |  |  |  |  | CHEVRON ACKERLY TAP |  |  |  |  |  | 0 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | ACHEV |  |  |  |  |  |  |  | CHEVRON ACKERLY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | BSCRM |  |  |  |  |  |  |  | BIG SPRING CRMWD |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | KNOTT |  |  |  |  |  |  |  | KNOTT |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 38 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | EMMA |  |  |  |  |  |  |  | EMMA |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | ANDRT |  |  |  |  |  |  |  | SAN ANDRES TAP |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MDFRM |  |  |  |  |  |  |  | MIDLAND FARMS |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SNAND |  |  |  |  |  |  |  | SAN ANDRES |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 45 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | ECTTP |  |  |  |  |  |  |  | ECTOR SHELL TAP |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | GSMTH |  |  |  |  |  |  |  | GOLDSMITH |  |  |  |  |  | 3 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | ODBSN |  |  |  |  |  |  |  | ODESSA BASIN |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | ECTSH |  |  |  |  |  |  |  | ECTOR SHELL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NumUBus | Islandnum | Fcomp | Fstatus |  |  |  |  | Fkv |  |  |  |  | Fstn |  |  |  |  |  |  |  | stnname |  |  |  |  |  | FBLI |  |  |  | RTUpref |  |  |  |  |  |  |  | N |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | GLDTP |  |  |  |  |  |  |  | GOLDSMITH TAP |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | GSCHV |  |  |  |  |  |  |  | GOLDSMITH CHEVRON |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 58 | AEP | b |  |  |  |  | 69 |  |  |  |  | ABON |  |  |  |  |  |  |  | ABILENE ONYX REA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | ANSO |  |  |  |  |  |  |  | ANSON REA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | DELT |  |  |  |  |  |  |  | DELK TAYLOR COOP |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | EXHA |  |  |  |  |  |  |  | EXXON HAWLEY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | ONYS |  |  |  |  |  |  |  | ONYX SWITCHING STATI |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 59 | AEP | b |  |  |  |  | 69 |  |  |  |  | GLSB |  |  |  |  |  |  |  | GOULDBUSK |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | HUMB |  |  |  |  |  |  |  | HUMBLE BALLINGER |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | ATTA |  |  |  |  |  |  |  | ATLANTIC TALPA |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | NOVC |  |  |  |  |  |  |  | NOVICE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | VALE |  |  |  |  |  |  |  | VALERA HUMBLE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 60 | AEP | b |  |  |  |  | 69 |  |  |  |  | ASPM |  |  |  |  |  |  |  | ASPERMONT CSW |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | PEAC |  |  |  |  |  |  |  | PEACOCK |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | TXHA |  |  |  |  |  |  |  | TEX HARVEY |  |  |  |  |  | 2 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | CONA |  |  |  |  |  |  |  | ASPERMONT CONTINENTA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SHHA |  |  |  |  |  |  |  | HAMLIN SHELL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SWEN |  |  |  |  |  |  |  | SWENSON STATION |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 62 | AEP | b |  |  |  |  | 69 |  |  |  |  | ALPI |  |  |  |  |  |  |  | ALPINE |  |  |  |  |  | 2 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | ALPR |  |  |  |  |  |  |  | ALPINE REA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | COCS |  |  |  |  |  |  |  | CONOCO COMP STATION |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | RGEC | U |  |  |  |  | 69 |  |  |  |  | ALTUDA |  |  |  |  |  |  |  | ALTUDA |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | PRSMNGAP |  |  |  |  |  |  |  | PERSIMMON GAP |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | TNMP | U |  |  |  |  | 69 |  |  |  |  | BELD |  |  |  |  |  |  |  | BELDING |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 68 | AEP | b |  |  |  |  | 69 |  |  |  |  | CRM3 |  |  |  |  |  |  |  | COLRDO RVR MUNICIPL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | CRM4 |  |  |  |  |  |  |  | COLRDO RVR MUNICIPL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | CRM5 |  |  |  |  |  |  |  | COLRDO RVR MUNICIPL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SAGT |  |  |  |  |  |  |  | SAN ANGELO GRAPE CRE |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | AMCO |  |  |  |  |  |  |  | AMOCO CSW |  |  |  |  |  | 1 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | CBRT |  |  |  |  |  |  |  | CARLSBAD TAP |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SAGC |  |  |  |  |  |  |  | SAN ANGELO GRAPE CRE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 75 | AEP | b |  |  |  |  | 69 |  |  |  |  | BARN |  |  |  |  |  |  |  | BARNHART |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | TANK |  |  |  |  |  |  |  | TANKERSLEY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | MERR |  |  |  |  |  |  |  | MERTZON REA TAP |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MERT |  |  |  |  |  |  |  | MERTZON |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | PHBA |  |  |  |  |  |  |  | PHILLIP BARNHART |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 78 | AEP | b |  |  |  |  | 69 |  |  |  |  | SGSA |  |  |  |  |  |  |  | SARAGOSA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | TRAN |  |  |  |  |  |  |  | TRANS PECOS |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | CCRK |  |  |  |  |  |  |  | CHERRY CREEK |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | CCRT |  |  |  |  |  |  |  | CHERRY CREEK TAP |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | VERH |  |  |  |  |  |  |  | VERHALEN |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 88 | AEP | b |  |  |  |  | 69 |  |  |  |  | CAMPWOOD |  |  |  |  |  |  |  | CAMPWOOD |  |  |  |  |  | 1 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | ROCKSPRS |  |  |  |  |  |  |  | ROCKSPRINGS |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | KIMBLE |  |  |  |  |  |  |  | KIMBLE COOP |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | ROCK_ATL |  |  |  |  |  |  |  | ROCKSPRINGS ATL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | LCRA | b |  |  |  |  | 69 |  |  |  |  | UTOPIA |  |  |  |  |  |  |  | UTOPIA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | LEAKEY |  |  |  |  |  |  |  | LEAKEY |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NumUBus | Islandnum | Fcomp | Fstatus |  |  |  |  | Fkv |  |  |  |  | Fstn |  |  |  |  |  |  |  | stnname |  |  |  |  |  | FBLI |  |  |  | RTUpref |  |  |  |  |  |  |  | N |  |  |  |  |  |  |  |  |  |  |
|  | 98 | AEP | b |  |  |  |  | 138 |  |  |  |  | MV_BURNS |  |  |  |  |  |  |  | MVEC (BURNS) |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | WESLACO |  |  |  |  |  |  |  | WESLACO SWITCH |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | GANDY |  |  |  |  |  |  |  | GANDY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MV_HBRG4 |  |  |  |  |  |  |  | MVEC (HEIDELBURG) |  |  |  |  |  | 1 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MV_WESL4 |  |  |  |  |  |  |  | MVEC (WESLACO) |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 99 | AEP | b |  |  |  |  | 69 |  |  |  |  | MV_FAYSW |  |  |  |  |  |  |  | MVEC (FAYSVILLE SWIT |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | MV_COOK1 |  |  |  |  |  |  |  | MVEC (McCOOK 1) |  |  |  |  |  | 1 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MV_COOK2 |  |  |  |  |  |  |  | MVEC (McCOOK 2) |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MV_FAYVL |  |  |  |  |  |  |  | MVEC (FAYSVILLE) |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 102 | AEP | b |  |  |  |  | 138 |  |  |  |  | MV_WEDN4 |  |  |  |  |  |  |  | MVEC (NW EDNBURG 138 |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | PHARMVEC |  |  |  |  |  |  |  | PHARR MVEC |  |  |  |  |  | 2 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | MERETT |  |  |  |  |  |  |  | MERETT |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MV_ALTON |  |  |  |  |  |  |  | MVEC (ALTON) |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MV_PALM4 |  |  |  |  |  |  |  | MVEC (PALMHURST) |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 131 | LCRA | b |  |  |  |  | 69 |  |  |  |  | SHERID |  |  |  |  |  |  |  | SHERIDAN |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | THORSW |  |  |  |  |  |  |  | THORSTENBURG |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | PARKBR |  |  |  |  |  |  |  | PARKER BROTHERS |  |  |  |  |  | 1 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | ROCKIS |  |  |  |  |  |  |  | ROCK ISLAND |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | THOR2 |  |  |  |  |  |  |  | THORSTENBURG TAP 2 |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 132 | LCRA | b |  |  |  |  | 69 |  |  |  |  | QUANSW |  |  |  |  |  |  |  | QUANEX SWITCH |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 138 |  |  |  |  | PRAIVI |  |  |  |  |  |  |  | PRAIRIE VIEW |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | PRAIVI |  |  |  |  |  |  |  | PRAIRIE VIEW |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SUNNYS |  |  |  |  |  |  |  | SUNNYSIDE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 138 |  |  |  |  | SEAWAY |  |  |  |  |  |  |  | SEAWAY LCRA |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 133 | LCRA | b |  |  |  |  | 69 |  |  |  |  | LKWDTP |  |  |  |  |  |  |  | LAKEWOOD TAP |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SMILGO |  |  |  |  |  |  |  | SMILEY GOAB |  |  |  |  |  | 0 |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | COST |  |  |  |  |  |  |  | COST |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | LAKEWD |  |  |  |  |  |  |  | LAKEWOOD LCRA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SMILEY |  |  |  |  |  |  |  | SMILEY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 | 7 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | SADLR |  |  |  |  |  |  |  | SADLER |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | GDNVL |  |  |  |  |  |  |  | GORDONVILLE TU |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  | RCEC | U |  |  |  |  | 69 |  |  |  |  | SHRWD_RC |  |  |  |  |  |  |  | SHERWOOD RC |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 14 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | BARRY |  |  |  |  |  |  |  | BARRY TU |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MRTNS |  |  |  |  |  |  |  | MERTENS |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | BLMGR |  |  |  |  |  |  |  | BLOOMING GROVE |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | TXEQL |  |  |  |  |  |  |  | TEXACO EQUILON |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 16 | ONCOR | b |  |  |  |  | 138 |  |  |  |  | GPMET |  |  |  |  |  |  |  | GRAPELAND MAGNOLIA E |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | GPLMG |  |  |  |  |  |  |  | GRAPELAND MAGNOLIA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | GPMEP |  |  |  |  |  |  |  | GRAPELAND MAGNOLIA E |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 18 | ONCOR | b |  |  |  |  | 138 |  |  |  |  | VTRTP |  |  |  |  |  |  |  | VETROTEX TAP |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | CNTED |  |  |  |  |  |  |  | CERTAIN TEED |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | VTRTX |  |  |  |  |  |  |  | VETROTEX |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 23 | ONCOR | b |  |  |  |  | 138 |  |  |  |  | DKCTP |  |  |  |  |  |  |  | DUCK CREEK TAP |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | DKCRK |  |  |  |  |  |  |  | DUCK CREEK |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | LHPMP |  |  |  |  |  |  |  | LAKE HUBBARD RAW WAT |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 25 | ONCOR | b |  |  |  |  | 138 |  |  |  |  | EFPMP |  |  |  |  |  |  |  | ELM FORK PUMP |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | EFPNR |  |  |  |  |  |  |  | ELM FORK PUMP NORTH |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NumUBus | Islandnum | Fcomp | Fstatus |  |  |  |  | Fkv |  |  |  |  | Fstn |  |  |  |  |  |  |  | stnname |  |  |  |  |  | FBLI |  |  |  | RTUpref |  |  |  |  |  |  |  | N |  |  |  |  |  |  |  |  |  |  |
|  | 35 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | AMOTP |  |  |  |  |  |  |  | AMOCO TAP |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | CLBSN |  |  |  |  |  |  |  | COLORADO BASIN |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | AMOCO |  |  |  |  |  |  |  | AMOCO TU |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | CGRGF |  |  |  |  |  |  |  | CHINA GROVE GULF |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 42 | AEP | b |  |  |  |  | 69 |  |  |  |  | SNTX1 |  |  |  |  |  |  |  | SYNTEX |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | MECPLNVW |  |  |  |  |  |  |  | MEC PLAINVIEW |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SNTXTAP |  |  |  |  |  |  |  | SYNTEX TAP |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  | ONCOR | b |  |  |  |  | 69 |  |  |  |  | PLVWT |  |  |  |  |  |  |  | PLAINVIEW |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 44 | ONCOR | b |  |  |  |  | 138 |  |  |  |  | BRAND |  |  |  |  |  |  |  | BRAND TU |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | ECRSW |  |  |  |  |  |  |  | ENNIS CREEK SWITCH |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SCPNZ |  |  |  |  |  |  |  | SCURRY PENNZOIL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | BUEYE |  |  |  |  |  |  |  | BULLSEYE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | ENCRT |  |  |  |  |  |  |  | ENNIS CREEK TAP |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 46 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | FKLCY |  |  |  |  |  |  |  | FRANKEL CITY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | FLRTN |  |  |  |  |  |  |  | FULLERTON |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | ANPHL |  |  |  |  |  |  |  | ANDREWS PHILLIPS |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | FLTEX |  |  |  |  |  |  |  | FULLERTON EXXON |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 50 | BEPC | b |  |  |  |  | 69 |  |  |  |  | CAPSCRNR |  |  |  |  |  |  |  | CAPPS CORNER |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | ALCORN |  |  |  |  |  |  |  | ALCORN |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | NOCONA |  |  |  |  |  |  |  | NOCONA TMPP |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  | 63 | AEP | b |  |  |  |  | 69 |  |  |  |  | FLOM |  |  |  |  |  |  |  | FLOMOT |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | TURK |  |  |  |  |  |  |  | TURKEY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | TURL |  |  |  |  |  |  |  | TURKEY LIGHTHOUSE |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  | 66 | AEP | b |  |  |  |  | 69 |  |  |  |  | ELYT |  |  |  |  |  |  |  | ELY REA TAP |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | TRNT |  |  |  |  |  |  |  | TRENT |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | MERK |  |  |  |  |  |  |  | MERKEL |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MKLT |  |  |  |  |  |  |  | SCOTT REA TAP |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 76 | AEP | b |  |  |  |  | 69 |  |  |  |  | SUNV |  |  |  |  |  |  |  | SUN VALLEY COOP |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | MAST |  |  |  |  |  |  |  | MASTERSON FIELD |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | PECV |  |  |  |  |  |  |  | PECOS VALLEY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | TNMP | b |  |  |  |  | 69 |  |  |  |  | GOMZ |  |  |  |  |  |  |  | GOMEZ |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 80 | AEP | b |  |  |  |  | 69 |  |  |  |  | HULD |  |  |  |  |  |  |  | HULLDALE SWTEC |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SANW |  |  |  |  |  |  |  | SAN ANGELO LAKE NASW |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | AROT |  |  |  |  |  |  |  | ARROTT |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | CRIS |  |  |  |  |  |  |  | CHRISTOVAL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 85 | AEP | b |  |  |  |  | 69 |  |  |  |  | BERCLAIR |  |  |  |  |  |  |  | BERCLAIR |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | FANNIN |  |  |  |  |  |  |  | FANNIN CSW |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | GOLIAD |  |  |  |  |  |  |  | GOLIAD |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  | STEC | b |  |  |  |  | 69 |  |  |  |  | FANNINS |  |  |  |  |  |  |  | FANNIN |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 86 | AEP | b |  |  |  |  | 69 |  |  |  |  | GARWOOD |  |  |  |  |  |  |  | GARWOOD |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | LAKESIDP |  |  |  |  |  |  |  | LAKEWOOD CSW |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | LONE_STR |  |  |  |  |  |  |  | LONE STAR CSW |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MATTHEWS |  |  |  |  |  |  |  | MATTHEWS |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 93 | AEP | b |  |  |  |  | 138 |  |  |  |  | LOPENO |  |  |  |  |  |  |  | LOPENO |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | S_YGANCI |  |  |  |  |  |  |  | SAN YGNACIO |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | RANDADO |  |  |  |  |  |  |  | RANDADO MEC |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | ZAPATA |  |  |  |  |  |  |  | ZAPATA |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
| NumUBus | Islandnum | Fcomp | Fstatus |  |  |  |  | Fkv |  |  |  |  | Fstn |  |  |  |  |  |  |  | stnname |  |  |  |  |  | FBLI |  |  |  | RTUpref |  |  |  |  |  |  |  | N |  |  |  |  |  |  |  |  |  |  |
|  | 95 | AEP | b |  |  |  |  | 138 |  |  |  |  | LGE |  |  |  |  |  |  |  | GREGORY POWER |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 14 |  |  |  |  | LGE |  |  |  |  |  |  |  | GREGORY POWER |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 138 |  |  |  |  | REYSHERW |  |  |  |  |  |  |  | REYNOLDS SHERWIN |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 96 | AEP | b |  |  |  |  | 138 |  |  |  |  | MV_HW511 |  |  |  |  |  |  |  | MVEC (HWY 511) |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MV_RIOHO |  |  |  |  |  |  |  | MVEC (E RIO HONDO) |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | COFFPORT |  |  |  |  |  |  |  | COFFEEPORT |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MV_CNTRA |  |  |  |  |  |  |  | MVEC (CENTRAL) |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 97 | AEP | b |  |  |  |  | 69 |  |  |  |  | RANGERVL |  |  |  |  |  |  |  | RANGERVILLE |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | S_MCALLN |  |  |  |  |  |  |  | SOUTH MCALLEN |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | HIDALGO |  |  |  |  |  |  |  | HIDALGO |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | RIO_RICO |  |  |  |  |  |  |  | RIO RICO |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 100 | AEP | b |  |  |  |  | 138 |  |  |  |  | MV_RAYVL |  |  |  |  |  |  |  | MVEC (RAYMONDVILLE T |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | MV_ERAY2 |  |  |  |  |  |  |  | MVEC (E RAYMONDVILLE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MV_LASAR |  |  |  |  |  |  |  | MVEC (LA SARA) |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 115 | CNP | b |  |  |  |  | 138 |  |  |  |  | _EX |  |  |  |  |  |  |  | EXPLOR |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | GBY |  |  |  |  |  |  |  | GREENS BAYOU |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | _UV |  |  |  |  |  |  |  | UVALDE REIT |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  | 119 | CNP | b |  |  |  |  | 69 |  |  |  |  | _RI |  |  |  |  |  |  |  | RICHMOND IRRIGATION |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | _RI |  |  |  |  |  |  |  | RICHMOND IRRIGATION |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | CIN |  |  |  |  |  |  |  | COLLIN |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 121 | CNP | b |  |  |  |  | 69 |  |  |  |  | AGR |  |  |  |  |  |  |  | AGRI |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | MIN |  |  |  |  |  |  |  | MINING |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 4 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  | 128 | LCRA | b |  |  |  |  | 69 |  |  |  |  | SANSAS |  |  |  |  |  |  |  | SAN SABA SWITCH |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | RICHSP |  |  |  |  |  |  |  | RICHLAND SPRINGS |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | TERRY |  |  |  |  |  |  |  | TERRY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 130 | LCRA | b |  |  |  |  | 69 |  |  |  |  | KING_2 |  |  |  |  |  |  |  | KINGSLAND 2 |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | KING_1 |  |  |  |  |  |  |  | KINGSLAND 1 |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SUNRBE |  |  |  |  |  |  |  | SUNRISE BEACH |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 136 | LCRA | b |  |  |  |  | 138 |  |  |  |  | GPISWI |  |  |  |  |  |  |  | GPI SWITCH |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | GPI |  |  |  |  |  |  |  | GPI |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 | 5 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | CHICC |  |  |  |  |  |  |  | CHICO CITY SERVICES |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | JKSBR |  |  |  |  |  |  |  | JACKSBORO TU |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | JKSAM |  |  |  |  |  |  |  | JACKSBORO AMOCO |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9 | ONCOR | b |  |  |  |  | 138 |  |  |  |  | LKVEW |  |  |  |  |  |  |  | LAKEVIEW |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  | RCEC | U |  |  |  |  | 138 |  |  |  |  | S_PAL_RC |  |  |  |  |  |  |  | SOUTH PALESTINE POD |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10 | BEPC | b |  |  |  |  | 138 |  |  |  |  | TAM |  |  |  |  |  |  |  | TEXAS AM |  |  |  |  |  | 4 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  | ONCOR | U |  |  |  |  | 138 |  |  |  |  | NGATECS |  |  |  |  |  |  |  | NORTHGATE COLLEGE ST |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 12 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | JKREA |  |  |  |  |  |  |  | JACKSBORO REA |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | JKSSN |  |  |  |  |  |  |  | JACKSBORO SINCLAIR |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 17 | BEPC | U |  |  |  |  | 138 |  |  |  |  | ZEPHYR |  |  |  |  |  |  |  | ZEPHYR TMPP |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | ONCOR | b |  |  |  |  | 138 |  |  |  |  | ZEPHR |  |  |  |  |  |  |  | ZEPHYR TU |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 19 | BEPC | U |  |  |  |  | 138 |  |  |  |  | NEWPORT |  |  |  |  |  |  |  | NEWPORT TMPP |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | ONCOR | b |  |  |  |  | 138 |  |  |  |  | LKARH |  |  |  |  |  |  |  | LAKE ARROWHEAD |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SNSSW |  |  |  |  |  |  |  | SUNSET SWITCH |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 21 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | CRWLY |  |  |  |  |  |  |  | CROWLEY |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
| NumUBus | Islandnum | Fcomp | Fstatus |  |  |  |  | Fkv |  |  |  |  | Fstn |  |  |  |  |  |  |  | stnname |  |  |  |  |  | FBLI |  |  |  | RTUpref |  |  |  |  |  |  |  | N |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | CRSSN |  |  |  |  |  |  |  | CRESSON |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 22 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | DSHAM |  |  |  |  |  |  |  | DIAMOND SHAMROCK |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | WFBSN |  |  |  |  |  |  |  | WICHITA FALLS BASIN |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 24 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | BRKTN |  |  |  |  |  |  |  | BROOKSTON |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | WINDM |  |  |  |  |  |  |  | WINDOM REA |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | HNYGR |  |  |  |  |  |  |  | HONEY GROVE |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 30 | ONCOR | b |  |  |  |  | 138 |  |  |  |  | MGIND |  |  |  |  |  |  |  | MG INDUSTRIES |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | WXPM2 |  |  |  |  |  |  |  | WAXAHACHIE PUMP 2 |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | WXPM1 |  |  |  |  |  |  |  | WAXAHACHIE PUMP 1 |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 40 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | ACRLY |  |  |  |  |  |  |  | ACKERLY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SNBRG |  |  |  |  |  |  |  | SPARENBURG |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | ALYNT |  |  |  |  |  |  |  | ACKERLY LYNTEGAR |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 41 | ONCOR | b |  |  |  |  | 69 |  |  |  |  | WELCH |  |  |  |  |  |  |  | WELCH |  |  |  |  |  | 3 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | OXWCH |  |  |  |  |  |  |  | OXY WELCH |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 47 | ONCOR | b |  |  |  |  | 138 |  |  |  |  | DHIDE |  |  |  |  |  |  |  | DOLLARHIDE |  |  |  |  |  | 3 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | DHUNO |  |  |  |  |  |  |  | DOLLARHIDE UNOCAL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 48 | BEPC | U |  |  |  |  | 69 |  |  |  |  | BRYSON |  |  |  |  |  |  |  | BRYAN SOUTH |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | TNMP | b |  |  |  |  | 69 |  |  |  |  | BRYSNTN |  |  |  |  |  |  |  | BRYSON TNP |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 52 | BEPC | b |  |  |  |  | 69 |  |  |  |  | ACT |  |  |  |  |  |  |  | ACTON |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  | BRYN | U |  |  |  |  | 69 |  |  |  |  | BTU373 |  |  |  |  |  |  |  | BRYAN LD ACTON |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 53 | AEP | b |  |  |  |  | 69 |  |  |  |  | CLRM |  |  |  |  |  |  |  | CLAIRMONT CSW |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  | BEPC | U |  |  |  |  | 69 |  |  |  |  | CLARMNT |  |  |  |  |  |  |  | CLAIRMONT TMPP |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 55 | BEPC | b |  |  |  |  | 69 |  |  |  |  | PURDON |  |  |  |  |  |  |  | PURDON |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | EMMETT |  |  |  |  |  |  |  | EMMETT |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 56 | BRYN | b |  |  |  |  | 69 |  |  |  |  | ANNEX |  |  |  |  |  |  |  | AM ANNEX |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | STEELE_S |  |  |  |  |  |  |  | STEELE STORE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 65 | AEP | b |  |  |  |  | 69 |  |  |  |  | GRBC |  |  |  |  |  |  |  | GRAYBACK |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | WAGR |  |  |  |  |  |  |  | WAGGONER |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | HARR |  |  |  |  |  |  |  | HARROLD |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 69 | AEP | b |  |  |  |  | 69 |  |  |  |  | CRM1 |  |  |  |  |  |  |  | COLRDO RVR MUNICIPL |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | PTRK |  |  |  |  |  |  |  | PAINT ROCK |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | EOLA |  |  |  |  |  |  |  | EOLA |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 82 | AEP | b |  |  |  |  | 69 |  |  |  |  | LK_WTH |  |  |  |  |  |  |  | NORTH TEXAS PLANT |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | WTH_LVOK |  |  |  |  |  |  |  | LIVE OAK WEATHERFORD |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | WTH_RAIL |  |  |  |  |  |  |  | WEATHERFORD RAIL RD |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 89 | AEP | b |  |  |  |  | 69 |  |  |  |  | BONIVIEW |  |  |  |  |  |  |  | BONNIEVIEW |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | HEARD |  |  |  |  |  |  |  | HEARD |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | WOODSBOR |  |  |  |  |  |  |  | WOODSBORO |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 90 | AEP | b |  |  |  |  | 69 |  |  |  |  | RUNGE |  |  |  |  |  |  |  | RUNGE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | YORKTOWN |  |  |  |  |  |  |  | YORKTOWN |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | NORDHEIM |  |  |  |  |  |  |  | NORDHEIM |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 94 | AEP | b |  |  |  |  | 69 |  |  |  |  | CAL_WWKS |  |  |  |  |  |  |  | CALALLEN WATERWORKS |  |  |  |  |  | 3 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | STEVENS |  |  |  |  |  |  |  | STEVENS |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 101 | AEP | b |  |  |  |  | 138 |  |  |  |  | CAUSEWAY |  |  |  |  |  |  |  | CAUSEWAY |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | S_PADRE |  |  |  |  |  |  |  | SOUTH PADRE |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | SUNCHSE |  |  |  |  |  |  |  | SUNCHASE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 104 | TNMP | b |  |  |  |  | 69 |  |  |  |  | P66_2 |  |  |  |  |  |  |  | PHILLIPS PETROL #2 |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NumUBus | Islandnum | Fcomp | Fstatus |  |  |  |  | Fkv |  |  |  |  | Fstn |  |  |  |  |  |  |  | stnname |  |  |  |  |  | FBLI |  |  |  | RTUpref |  |  |  |  |  |  |  | N |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | P66_3 |  |  |  |  |  |  |  | PHILLIPS PETROL #3 |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | P66_4 |  |  |  |  |  |  |  | PHILLIPS PETROL #4 |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 106 | TNMP | b |  |  |  |  | 69 |  |  |  |  | PHLLPSOP |  |  |  |  |  |  |  | PHILLIPS ORIGIN PUMP |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | PHLLPSTF |  |  |  |  |  |  |  | PHILLIPS TANK FARM S |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 107 | TNMP | b |  |  |  |  | 69 |  |  |  |  | LIQDCARB |  |  |  |  |  |  |  | LIQUID CARBONICS SUB |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | MARTHNPL |  |  |  |  |  |  |  | MARATHON PIPELINE SU |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 111 | TNMP | b |  |  |  |  | 69 |  |  |  |  | HANDLEY |  |  |  |  |  |  |  | HANDLEY |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | VLLYMILS |  |  |  |  |  |  |  | VALLEY MILLS |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 112 | TNMP | b |  |  |  |  | 69 |  |  |  |  | SAINT_JO |  |  |  |  |  |  |  | SAINT JO |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | NOCONATN |  |  |  |  |  |  |  | NOCONA TNP |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 113 | TNMP | b |  |  |  |  | 69 |  |  |  |  | CORYELCO |  |  |  |  |  |  |  | CORYELL COUNTY TNP |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | GATESVL1 |  |  |  |  |  |  |  | GATESVILLE 1 |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 114 | CNP | b |  |  |  |  | 138 |  |  |  |  | DOW |  |  |  |  |  |  |  | DOW CHEMICAL |  |  |  |  |  | 3 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | DOWGEN |  |  |  |  |  |  |  | DOW CHEMICAL GEN |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 116 | CNP | b |  |  |  |  | 138 |  |  |  |  | PWL |  |  |  |  |  |  |  | POWELL REIT |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SEP |  |  |  |  |  |  |  | SEPTON |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | SHR |  |  |  |  |  |  |  | SHORE ACRES |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 118 | CNP | b |  |  |  |  | 138 |  |  |  |  | ATK |  |  |  |  |  |  |  | ARITEK |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | RNG |  |  |  |  |  |  |  | STRANG |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | RIN |  |  |  |  |  |  |  | CHORIN LA PORTE |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 120 | CNP | b |  |  |  |  | 138 |  |  |  |  | _JP |  |  |  |  |  |  |  | JACINTOPORT |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | DOL |  |  |  |  |  |  |  | DOWLAP |  |  |  |  |  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | BOR |  |  |  |  |  |  |  | BORDEN METALS |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 122 | CNP | b |  |  |  |  | 138 |  |  |  |  | BYR |  |  |  |  |  |  |  | BYPARK |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | HIM |  |  |  |  |  |  |  | HIMONT |  |  |  |  |  | 5 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 138 |  |  |  |  | LZB |  |  |  |  |  |  |  | LUZBAY |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 126 | LCRA | b |  |  |  |  | 69 |  |  |  |  | HALLGV |  |  |  |  |  |  |  | HALLETTSVILLE GVEC |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | HENKA |  |  |  |  |  |  |  | HENKHAUS |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SHINGV |  |  |  |  |  |  |  | SHINER GVEC |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | MOULGV |  |  |  |  |  |  |  | MOULTON GVEC |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 129 | LCRA | b |  |  |  |  | 69 |  |  |  |  | HARWOO |  |  |  |  |  |  |  | HARWOOD |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | WAELDE |  |  |  |  |  |  |  | WAELDER |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | THOMPS |  |  |  |  |  |  |  | THOMPSONVILLE |  |  |  |  |  | 1 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  | 134 | LCRA | b |  |  |  |  | 69 |  |  |  |  | HARPER |  |  |  |  |  |  |  | HARPER CTEC |  |  |  |  |  | 2 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | DOSS |  |  |  |  |  |  |  | DOSS |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 135 | LCRA | b |  |  |  |  | 69 |  |  |  |  | CANYON |  |  |  |  |  |  |  | CANYON LCRA |  |  |  |  |  | 0 |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | CENTEX |  |  |  |  |  |  |  | CENTEX |  |  |  |  |  | 4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | U |  |  |  |  | 69 |  |  |  |  | KYLE |  |  |  |  |  |  |  | KYLE |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

PUCT Substantive Rules 25.200